## Info
Reporting Period: |  |  | 1 |  | Maximum Validated Flow Rate: |  | 7
Treatment Plant: |  |  | 2 |  | Minimum Validated UVT: |  | 8
PWSID: |  |  | 3 |  | Target Pathogen: |  | 9
UV Reactor: |  |  | 4 |  | Required Log Inactivation1: |  | 10
Operator Signature: |  |  | 5 |  | Target Log Inactivation (Logi Setpoint)1: |  | 11
Date: |  |  | 6 |  | Dose Required for Target (Dreq'd) [A]2: |  | 12 | mJ/cm2
Operational Data |  |  |  | Data at Daily Minimum Validated Dose | [6 empty] | UV Dose Adequacy Determination | Total Off-Specification | Value No. | Tag Name | Method | Description
Day | Run Time (hours) | Total Production (MG) |  | Time of Minimum Validated Dose | Validation Factor [VF] for UVT at Minimum Dose | MS2 RED3 (mJ/cm2) [B] | Daily Minimum Validated Dose4 ([B]/[VF]) (mJ/cm2) [C] |  | Flow Rate (MGD) | UVT (%) | Validated Dose>Dreq'd ([C]>[A]) (Y/N) | Total Off-Specification Volume (MG) | 1 |  | Calculated | Reporting period calculated based off the date entered in Cell F7 on "January" sheet.
13 | 14 | 15 |  | 16 | 17 | 18 | 19 |  | 20 | 21 | 22 | 23 | 2 |  | Fixed | Treatment plant name is a fixed value.
Min | 24 | 25 |  |  | 26 | 27 | 28 |  | 29 | 30 |  |  | 3 |  | Fixed | PWSID is a fixed value.
Max | 31 | 32 |  |  | 33 | 34 | 35 |  | 36 | 37 |  |  | 4 |  | Fixed | UV reactor unit number is a fixed value.
Total | 38 | 39 | [9 empty] | 40 | 5 |  | Manual | Operator signature to be manually entered by user.
[13 empty] | 6 |  | Calculated | Date value is calculated as the time when report is generated.
[13 empty] | 7 |  | Fixed | Maximum validated flow rate is fixed at 1,518 gpm for the Trojan UVSwiftSC D06 UV reactor.
[13 empty] | 8 |  | Fixed | Minimum validated UVT is fixed at 70.0% for the Trojan UVSwiftSC D06 UV reactor.
[13 empty] | 9 | [TAG NAME] | Calculated | Determines target pathogen (Cryptosporidium or Giardia) based on value selected at UV HMI.
[13 empty] | 10 |  | Fixed | Required log inactivation for Giardia and Cryptosporidum fixed at 3.0-log.
[13 empty] | 11 |  | Manual | Target log inactivation setpoint to be manually entered by user.
[13 empty] | 12 |  | Manual | Dose required for target log inactivation setpoint to be manually entered by user.
[13 empty] | 13 |  | Fixed | Day of the month is a fixed value.
[13 empty] | 14 | [TAG NAME] | Calculated | Returns the daily total run time.
[13 empty] | 15 | [TAG NAME] | Calculated | Returns the daily total production volume.
[13 empty] | 16 | [TAG NAME] | Calculated | Returns the time at which the daily minimum validated dose occurs for the target pathogen.
[13 empty] | 17 | [TAG NAME] | Calculated | Returns the Validation Factor at the time of the minimum validated dose for the target pathogen.
[13 empty] | 18 | [TAG NAME] | Calculated | Returns the MS2 RED at the time of the minimum validated dose for the target pathogen.
[13 empty] | 19 |  | Calculated | Calculates the minimum validated dose by dividing the MS2 RED by the Validation Factor.
[13 empty] | 20 | [TAG NAME] | Calculated | Returns the flow rate through the reactor at the time of the minimum validated dose.
[13 empty] | 21 | [TAG NAME] | Calculated | Returns the UVT of the water at the time of the minimum validated dose.
[13 empty] | 22 |  | Calculated | Determines if the minimum validated dose for the day is greater than the dose required for target.
[13 empty] | 23 | [TAG NAME] | Calculated | Sum of water production during off-specification events during the day lasting longer than 120 seconds.
[13 empty] | 24 |  | Calculated | Calculates the minimum daily run time for the month.
[13 empty] | 25 |  | Calculated | Calculates the minimum daily production for the month.
[13 empty] | 26 |  | Calculated | Calculates the minimum daily Validation Factor at the time of the minimum validated dose for the month.
[13 empty] | 27 |  | Calculated | Calculates the minimum daily MS2 RED at the time of the minimum validated dose for the month.
[13 empty] | 28 |  | Calculated | Calculates the minimum daily vailidated dose for the month.
[13 empty] | 29 |  | Calculated | Calculates the minimum daily flow rate at the time of the minimum validated dose for the month.
[13 empty] | 30 |  | Calculated | Calculates the minimum daily UVT at the time of the minimum validated dose for the month.
[13 empty] | 31 |  | Calculated | Calculates the maximum daily run time for the month.
[13 empty] | 32 |  | Calculated | Calculates the maximum daily production for the month.
[13 empty] | 33 |  | Calculated | Calculates the maximum daily Validation Factor at the time of the minimum validated dose for the month.
[13 empty] | 34 |  | Calculated | Calculates the maximum daily MS2 RED at the time of the minimum validated dose for the month.
[13 empty] | 35 |  | Calculated | Calculates the maximum daily vailidated dose for the month.
[13 empty] | 36 |  | Calculated | Calculates the maximum daily flow rate at the time of the minimum validated dose for the month.
[13 empty] | 37 |  | Calculated | Calculates the maximum daily UVT at the time of the minimum validated dose for the month.
[13 empty] | 38 |  | Calculated | Calculates the total run time for the reactor for the month.
[13 empty] | 39 |  | Calculated | Calculates the total production through the reactor for the month.
[13 empty] | 40 |  | Calculated | Calculates the total off-specification volume produced by the reactor for the month.

## Summary
Reporting Period: |  |  |  |  | Maximum Validated Flow Rate: |  | 1,559.8 gpm
Treatment Plant: |  |  | Creekside WTP |  | Minimum Validated UVT: |  | 68.4%
PWSID: |  |  | UT22011 |  | Target Pathogen: |  | Giardia
UV Reactor: |  |  | UVR-46011 |  | Required Log Inactivation1: |  | 0.5
Operator Signature: |  |  |  |  | Target Log Inactivation (Logi Setpoint)1: |  | 0.5
Date: |  |  |  |  | Dose Required for Target (Dreq'd) [A]2: |  | 1.5 | mJ/cm2
Operational Data |  |  |  | Data at Daily Minimum Validated Dose | [6 empty] | UV Dose Adequacy Determination | Total Off-Specification
Day | Run Time (hours) | Total Production (MG) |  | Time of Minimum Validated Dose | Validation Factor [VF] for UVT at Minimum Dose | MS2 RED3 (mJ/cm2) [B] | Daily Minimum Validated Dose4 ([B]/[VF]) (mJ/cm2) [C] |  | Flow Rate (MGD) | UVT (%) | Validated Dose>Dreq'd ([C]>[A]) (Y/N) | Total Off-Specification Volume (MG)
1 |  |  |  |  | 3.66
2 |  |  |  |  | 3.66
3 |  |  |  |  | 3.66
4 |  |  |  |  | 3.66
5 |  |  |  |  | 3.66
6 |  |  |  |  | 3.66
7 |  |  |  |  | 3.66
8 |  |  |  |  | 3.66
9 |  |  |  |  | 3.66
10 |  |  |  |  | 3.66
11 |  |  |  |  | 3.66
12 |  |  |  |  | 3.66
13 |  |  |  |  | 3.66
14 |  |  |  |  | 3.66
15 |  |  |  |  | 3.66
16 |  |  |  |  | 3.66
17 |  |  |  |  | 3.66
18 |  |  |  |  | 3.66
19 |  |  |  |  | 3.66
20 |  |  |  |  | 3.66
21 |  |  |  |  | 3.66
22 |  |  |  |  | 3.66
23 |  |  |  |  | 3.66
24 |  |  |  |  | 3.66
25 |  |  |  |  | 3.66
26 |  |  |  |  | 3.66
27 |  |  |  |  | 3.66
28 |  |  |  |  | 3.66
29 |  |  |  |  | 3.66
30 |  |  |  |  | 3.66
31 |  |  |  |  | 3.66
Min |  |  |  |  | 3.66
Max |  |  |  |  | 3.66
Total
1 Required Log Inactivation is what is necessary to achieve regulatory compliance for the Target Pathogen. Target Log Inactivation is the operational setpoint for the UV Reactor.
2 Dreq'd is the dose required for the Target Log Inactivation without a Validation Factor or Sensor Correction Factor applied and can be found in the UVDGM Table 1.4.
3 MS2 RED is the Reduction Equivalent Dose calculated using the dose algorithm in the PLC.
4 The Validated Dose is the dose based on the calculated dose that is normalized on the Validation Factor and the Correction Factor.
5 UV Off-Specification Water Log should be used to calculate and report daily off-specification volume. If UVT, flowrate, and/or Validated Dose off-specification occur simultaneously, the off-specification time should only be counted once.
Note on B42: Zalla, Joseph/SLC: Excel calculated value.
Note on B43: Zalla, Joseph/SLC: Excel calculated value.
Note on B44: Zalla, Joseph/SLC: Excel calculated value.