## EPA Monthly Summary
LT1SWTR MONTHLY REPORT TO EPA FOR COMPLIANCE DETERMINATION
(Due to EPA by 10th day of the following month)
Month | 7 |  | System/Treatment Plant |  |  |  | Creekside Water Treatment Plant | [8 empty] | PWSID |  |  |  | 22011
Year | 2017 |  | Type of Filtration |  |  |  | Cartridge Filtration
Combined Effluent Turbidity Performance Criteria (Data in 'Turbidity Data' Worksheet)
A. Total number of Combined Filter Effluent (CFE) water turbidity measurements = | [12 empty] | 121
B. Total Number of CFE water turbidity measurements that are less than or equal to 0.3 NTU = | [16 empty] | 121
C. The percentage of CFE turbidity measurements meeting 0.3 NTU = B / A * 100 = | [13 empty] | 100 |  |  |  | %
D. Record the date and turbidity value for any CFE measurements exceeding 1 NTU: If none, enter “none” below:
E. Total number of chlorine residual measurements: | [9 empty] | 26
| Time and Date of Exceedance |  |  |  |  | Highest Turbidity (NTU) |  |  |  |  | Time and Date EPA Was Notified
None
Disinfection Performance Criteria
A. Point-of-Entry Minimum Disinfectant Residual Criteria and CT Criteria
The minimum residual concentration must not drop below 0.2 mg/L OR the higher value (>0.2 mg/L) needed each day for adequate inactivation of viruses.
Date | Minimum Disinfectant Residual at Point of Entry to Distribution System (mg/L) |  |  |  | Date |  |  | Minimum Disinfectant Residual at Point of Entry to Distribution System (mg/L) |  |  |  | Date |  | Minimum Disinfectant Residual at Point of Entry to Distribution System (mg/L)
7/1 | 2.098 |  |  |  | 7/11 |  |  | 2.1533 |  |  |  | 7/21 |  | 2.11
7/2 | 1.9056 |  |  |  | 7/12 |  |  | 1.693 |  |  |  | 7/22 |  | 2.1329
7/3 | 1.7958 |  |  |  | 7/13 |  |  | 1.5627 |  |  |  | 7/23 |  | 2.1258
7/4 | 1.7338 |  |  |  | 7/14 |  |  | 1.8992 |  |  |  | 7/24 |  | 2.119
7/5 | 1.7889 |  |  |  | 7/15 |  |  | 1.8649 |  |  |  | 7/25 |  | 2.0706
2017-07-06 | PO |  |  |  | 7/16 |  |  | 1.7548 |  |  |  | 7/26 |  | 1.8023
7/7 | PO |  |  |  | 7/17 |  |  | 1.8236 |  |  |  | 7/27 |  | 1.768
2017-07-08 | PO |  |  |  | 7/18 |  |  | 2.0025 |  |  |  | 7/28 |  | 1.871
2017-07-09 | PO |  |  |  | 7/19 |  |  | 1.3837 |  |  |  | 7/29 |  | 1.9881
2017-07-10 | PO |  |  |  | 7/20 |  |  | 1.6719 |  |  |  | 7/30 |  | 1.8368
[12 empty] | 7/31 |  | 2.0086
Days where the POE Residual Was < 0.2 mg/L for > 4 hours
Time/Day |  |  |  |  | Duration of Low Level (indicate hrs) | [6 empty] | Time and Date Reported to EPA
None
B. Distribution System Disinfectant Residual Criteria MEASURED WHEN TAKING TCR (BACT) SAMPLES
A = # of samples this month that disinfectant residual was measured in distribution system = | [18 empty] | 13
C = # of samples this month that disinfectant residual was NOT detected when you measured = | [18 empty] | 13
V = C / A * 100 = |  |  |  | 100 |  | % |  |  | For the previous month, V = |  |  | 100 |  |  |  | %
Prepared by |  | Michelle De Haan | [12 empty] | Date | 2017-08-02

## Turbidity Data
Monthly Report for Water Treatment Technique Compliance - Turbidity
| Month: | July |  |  |  |  | Utility Name: | Park City |  |  | Conventional
| Year: | 2017 |  |  |  |  | Treatment Plant: | Creekside Water Treatment Plant |  |  | Direct Filtration
| System Number: | #REF! |  |  |  |  | Filtration Technology: | Cartridge Filtration |  |  | Membrane Filtration
[7 empty] | Prepared by: | Iwona Goodley |  |  | Slow Sand Filtration
Cartridge Filtration
REQUIRED # OF 4-HOUR TURBIDITY READINGS/DAY = |  |  |  |  | 6 | (UNLESS PLANT OFF – INDICATE “PO” IN EACH CELL) |  |  |  |  | Bag Filtration
Diatomaceous Earth Filtration
**REPORT MAXIMUM TURBIDITY READING THAT DAY, EVEN IF IT WAS BETWEEN 4 HOUR READINGS | [10 empty] | Other (attach description)
None
DO NOT REPORT RESULTS COLLECTED DURING BACKWASH, FILTER-TO-WASTE, OR ANY TIME WATER IS NOT BEING PRODUCED FOR CONSUMPTION
4 Hour Combined Filter Turbidity Readings
| Hours | 1st - 4 hr | 2nd - 4 hr | 3rd - 4 hr | 4th - 4 hr | 5th - 4 hr | 6th - 4 hr | Daily | Number | Number
Date | of | Max NTU | Max NTU | Max NTU | Max NTU | Max NTU | Max NTU | Max | Readings | Turbidity
| Operation | Reading | Reading | Reading | Reading | Reading | Reading | (NTU) | <.3 NTU | Readings
7/1 | 12.67 | 0.13375 | 0.04125 | 0.034375 | 0.033125 | PO | PO | 0.13375 | 4 | 4
7/2 | 5.46 | 0.11312 | 0.07 | PO | PO | PO | 0.09625 | 0.11312 | 3 | 3
7/3 | 9.41 | 0.05375 | 0.035625 | 0.035 | PO | PO | PO | 0.05375 | 3 | 3
7/4 | 8.18 | 0.12125 | 0.036875 | 0.034375 | PO | PO | PO | 0.12125 | 3 | 3
7/5 | 11.16 | 0.1525 | 0.038125 | 0.035625 | PO | 0.206 | 0.038125 | 0.206 | 5 | 5
7/6 | 15.34 | 0.13313 | 0.03625 | 0.03375 | 0.034375 | PO | 0.2225 | 0.2225 | 5 | 5
7/7 | 18.87 | 0.04375 | 0.17937 | 0.12125 | 0.10063 | 0.040625 | 0.033125 | 0.17937 | 6 | 6
7/8 | 19.79 | 0.034375 | 0.035 | 0.033125 | 0.03375 | 0.0325 | 0.1475 | 0.1475 | 6 | 6
7/9 | 21.91 | 0.035 | 0.035625 | 0.040625 | 0.036875 | 0.11625 | 0.03625 | 0.11625 | 6 | 6
7/10 | 20.57 | 0.041875 | 0.035 | 0.038125 | 0.035625 | 0.165 | 0.03875 | 0.165 | 6 | 6
7/11 | 17.22 | 0.03625 | 0.0375 | 0.03625 | 0.11688 | 0.0925 | 0.11688 | 0.11688 | 6 | 6
7/12 | 12.91 | 0.10625 | 0.036875 | 0.10312 | 0.043125 | 0.036875 | PO | 0.10625 | 5 | 5
7/13 | 6.18 | 0.22062 | 0.035 | PO | PO | PO | PO | 0.22062 | 2 | 2
7/14 | 4.61 | PO | 0.15687 | 0.0525 | PO | PO | PO | 0.15687 | 2 | 2
7/15 | 3.97 | 0.098125 | 0.14062 | 0.035625 | PO | PO | PO | 0.14062 | 3 | 3
7/16 | 4.5 | 0.11 | 0.04125 | PO | PO | PO | PO | 0.11 | 2 | 2
7/17 | 10.12 | 0.20875 | 0.03875 | 0.038125 | PO | PO | PO | 0.20875 | 3 | 3
7/18 | 3.85 | 0.14187 | 0.04375 | PO | PO | PO | PO | 0.14187 | 2 | 2
7/19 | 7.65 | PO | 0.12125 | 0.041875 | 0.045625 | 0.0525 | PO | 0.12125 | 4 | 4
7/20 | 0 | PO | PO | PO | PO | PO | PO | PO | 0 | 0
7/21 | 6.76 | 0.18875 | 0.05125 | PO | PO | PO | PO | 0.18875 | 2 | 2
7/22 | 13.11 | 0.098125 | 0.14062 | 0.04125 | 0.03875 | 0.038125 | 0.045 | 0.14062 | 6 | 6
7/23 | 8.52 | 0.12188 | 0.084375 | 0.036875 | PO | PO | 0.18937 | 0.18937 | 4 | 4
7/24 | 10.32 | 0.048125 | 0.038125 | 0.036875 | PO | PO | 0.2175 | 0.2175 | 4 | 4
7/25 | 7.8 | 0.11312 | PO | 0.15 | 0.04 | 0.15812 | PO | 0.15812 | 4 | 4
7/26 | 0 | PO | PO | PO | PO | PO | PO | PO | 0 | 0
7/27 | 9.6 | PO | 0.21188 | 0.048125 | PO | 0.18063 | 0.048125 | 0.21188 | 4 | 4
7/28 | 15.99 | 0.040625 | 0.03875 | 0.11937 | 0.04625 | 0.03625 | 0.078125 | 0.11937 | 6 | 6
7/29 | 15.37 | 0.0375 | 0.035625 | 0.041875 | 0.090625 | 0.07125 | 0.039375 | 0.090625 | 6 | 6
7/30 | 10.72 | 0.0825 | 0.034375 | 0.035 | PO | PO | 0.088125 | 0.088125 | 4 | 4
7/31 | 15.77 | 0.088125 | 0.0875 | 0.088125 | PO | 0.08875 | 0.088125 | 0.08875 | 5 | 5
[8 empty] | Total Number of Turbidity Measurements Taken: | 121
[8 empty] | Total Number of Turbidity Less Than 0.3 NTU | 121
[8 empty] | Percent of Turbidity Measurements Less Than 0.3 NTU: | 100%
[9 empty] | Individual filter turbidity data (15 minute) compiled and checked for compliance (Y/N): | Y
Note on A10: Kunik, Erinn/SLC: Discuss maximum turbidity reading. The daily max reported in this spreadsheet and the QJ spreadsheet use the max of the reported values. I'm not sure how we'd have any readings between 4-hr readings since we are reading more frequently than every 15-minutes. We should make sure we are consistent between plants with how frequent we are grabbing this data and averaging or other calcs being applied. This info should be spelled out clearly so the user knows how results are calculated. Allen needs to provide the same verification report he provides for QJWTP filters.

## Operational Worksheet
4-HR VIRUS INACTIVATION CT WORKSHEET FOR INPUT TO MONTHLY REPORTING
CREEKSIDE WTP
|  |  | Plant Operating Data | [6 empty] | CT Calcs |  | RESULTS
Min Ratio for Day | Date and Time | Day | Park Meadows Flow Rate | Divide Flow Rate | Combined Park Meadows + Divide Flow Rate | Park Meadows pH | Park Meadows Temp. | Chlorine Residual from analyzer | Required CTr | Sequence 1 Effective Time | Sequence 1 Cta | Compliance Ratio | Status
|  |  | (gpm) | (gpm) | (gpm) |  | (Deg. F) | (mg/L) | (mg-min/L) | (min) | (mg-min/L) | CTa/CTr
| 7/1/2017 1:00 AM | 1 | 1350.1988 |  | 1350.1988 |  | 60.6646 | 2.2902 | 4 | 10.1618 | 23.2728 | 5.8182 | OK
| 7/1/2017 2:00 AM | 1 | 1342.3822 |  | 1342.3822 |  | 60.9897 | 2.2902 | 3.8 | 10.221 | 23.4083 | 6.1601 | OK
| 7/1/2017 3:00 AM | 1 | 1351.5909 |  | 1351.5909 |  | 62.6432 | 2.3177 | 3.6 | 10.1514 | 23.528 | 6.5356 | OK
| 7/1/2017 4:00 AM | 1 | 1341.9537 |  | 1341.9537 |  | 59.9297 | 2.3109 | 4 | 10.2243 | 23.6269 | 5.9067 | OK
| 7/1/2017 5:00 AM | 1 | 1332.852 |  | 1332.852 |  | 57.2621 | 2.3178 | 4.4 | 10.2941 | 23.8599 | 5.4227 | OK
| 7/1/2017 6:00 AM | 1 | 1361.303 |  | 1361.303 |  | 59.9226 | 2.311 | 4 | 10.079 | 23.2922 | 5.823 | OK
| 7/1/2017 7:00 AM | 1 | 1362.3739 |  | 1362.3739 |  | 61.1557 | 2.2972 | 3.8 | 10.071 | 23.1349 | 6.0881 | OK
| 7/1/2017 8:00 AM | 1 | 1354.0538 |  | 1354.0538 |  | 61.2653 | 2.3179 | 3.8 | 10.1329 | 23.4874 | 6.1809 | OK
| 7/1/2017 9:00 AM | 1 | 1362.406 |  | 1362.406 |  | 61.2971 | 2.2835 | 3.8 | 10.0708 | 22.9964 | 6.0517 | OK
| 7/1/2017 10:00 AM | 1 | 1357.234 |  | 1357.234 |  | 61.1593 | 2.2974 | 3.8 | 10.1092 | 23.2246 | 6.1117 | OK
| 7/1/2017 11:00 AM | 1 | 1350.7345 |  | 1350.7345 |  | 60.8413 | 2.3042 | 3.8 | 10.1578 | 23.406 | 6.1595 | OK
| 7/1/2017 12:00 PM | 1 | 1352.4476 |  | 1352.4476 |  | 60.5268 | 2.3042 | 4 | 10.145 | 23.3763 | 5.8441 | OK
| 7/1/2017 1:00 PM | 1 | 1362.299 |  | 1362.299 |  | 60.0357 | 2.2974 | 4 | 10.0716 | 23.1383 | 5.7846 | OK
| 7/1/2017 2:00 PM | 1 | 1352.9829 |  | 1352.9829 |  | 59.3573 | 2.3249 | 4 | 10.1409 | 23.5765 | 5.8941 | OK
| 7/1/2017 3:00 PM | 1 | 1357.9086 |  | 1357.9086 |  | 59.1736 | 2.325 | 4 | 10.1042 | 23.4921 | 5.873 | OK
| 7/1/2017 4:00 PM | 1 | 1354.5891 |  | 1354.5891 |  | 58.2408 | 2.2904 | 4.4 | 10.1289 | 23.1995 | 5.2726 | OK
| 7/1/2017 5:00 PM | 1 | 1367.9742 |  | 1367.9742 |  | 58.0712 | 2.2904 | 4.4 | 10.0298 | 22.9725 | 5.221 | OK
| 7/1/2017 6:00 PM | 1 | 1355.9812 |  | 1355.9812 |  | 57.5165 | 2.2837 | 4.4 | 10.1185 | 23.1075 | 5.2517 | OK
| 7/1/2017 7:00 PM | 1 | 1368.4024 |  | 1368.4024 |  | 56.9088 | 2.2871 | 4.8 | 10.0267 | 22.9321 | 4.7775 | OK
| 7/1/2017 8:00 PM | 1 | 1351.9441 |  | 1351.9441 |  | 56.1491 | 2.208 | 4.8 | 10.1487 | 22.4087 | 4.6685 | OK
| 7/1/2017 9:00 PM | 1 | 1364.4404 |  | 1364.4404 |  | 56.0891 | 2.215 | 4.8 | 10.0558 | 22.2734 | 4.6403 | OK
| 7/1/2017 10:00 PM | 1 | 1367.653 |  | 1367.653 |  | 56.3117 | 2.2012 | 4.8 | 10.0322 | 22.0826 | 4.6005 | OK
| 7/1/2017 11:00 PM | 1 | 1354.0538 |  | 1354.0538 |  | 59.2725 | 2.098 | 4 | 10.1329 | 21.259 | 5.3148 | OK
| 7/2/2017 12:00 AM | 2 | 1363.0484 |  | 1363.0484 |  | 59.2372 | 2.1117 | 4 | 10.0661 | 21.2566 | 5.3142 | OK
| 7/2/2017 1:00 AM | 2 | 1350.4129 |  | 1350.4129 |  | 58.7955 | 2.1117 | 4.4 | 10.1602 | 21.4555 | 4.8763 | OK
| 7/2/2017 2:00 AM | 2 | 1358.444 |  | 1358.444 |  | 62.887 | 2.098 | 3.6 | 10.1002 | 21.1903 | 5.8862 | OK
| 7/2/2017 3:00 AM | 2 | 1357.4802 |  | 1357.4802 |  | 64.1413 | 2.098 | 3.6 | 10.1073 | 21.2054 | 5.8904 | OK
| 7/2/2017 4:00 AM | 2 | 1359.515 |  | 1359.515 |  | 64.6784 | 2.098 | 3.4 | 10.0922 | 21.1736 | 6.2275 | OK
| 7/2/2017 5:00 AM | 2 | 1356.5167 |  | 1356.5167 |  | 65.0105 | 2.0981 | 3.4 | 10.1145 | 21.2215 | 6.2416 | OK
| 7/2/2017 6:00 AM | 2 | 1349.3424 |  | 1349.3424 |  | 64.8091 | 2.098 | 3.4 | 10.1683 | 21.3332 | 6.2745 | OK
| 7/2/2017 7:00 AM | 2 | 1357.6945 |  | 1357.6945 |  | 64.6395 | 2.1118 | 3.4 | 10.1057 | 21.3415 | 6.2769 | OK
| 7/2/2017 8:00 AM | 2 | 1326.32 |  | 1326.32 |  | 64.2685 | 2.1257 | 3.6 | 10.3448 | 21.9903 | 6.1084 | OK
| 7/2/2017 9:00 AM | 2 | 1346.665 |  | 1346.665 |  | 63.7527 | 2.0706 | 3.6 | 10.1885 | 21.0965 | 5.8602 | OK
| 7/2/2017 10:00 AM | 2 | 1351.3768 |  | 1351.3768 |  | 63.6219 | 2.0158 | 3.6 | 10.153 | 20.4667 | 5.6852 | OK
| 7/2/2017 11:00 AM | 2 | 1355.0173 |  | 1355.0173 |  | 62.9577 | 1.9608 | 3.6 | 10.1257 | 19.8547 | 5.5152 | OK
| 7/2/2017 12:00 PM | 2 | 1342.5963 |  | 1342.5963 |  | 62.675 | 1.9608 | 3.6 | 10.2194 | 20.0384 | 5.5662 | OK
| 7/2/2017 1:00 PM | 2 | 1358.5511 |  | 1358.5511 |  | 62.2051 | 1.9816 | 3.8 | 10.0994 | 20.0128 | 5.2665 | OK
| 7/2/2017 2:00 PM | 2 | 1369.4733 |  | 1369.4733 |  | 61.555 | 1.9747 | 3.8 | 10.0188 | 19.7845 | 5.2065 | OK
| 7/2/2017 3:00 PM | 2 | 1366.1536 |  | 1366.1536 |  | 61.0957 | 1.9608 | 3.8 | 10.0432 | 19.6929 | 5.1823 | OK
| 7/2/2017 4:00 PM | 2 | 1363.7982 |  | 1363.7982 |  | 60.7742 | 1.9678 | 4 | 10.0605 | 19.7969 | 4.9492 | OK
| 7/2/2017 5:00 PM | 2 | 1346.0228 |  | 1346.0228 |  | 60.223 | 1.9332 | 4 | 10.1934 | 19.706 | 4.9265 | OK
| 7/2/2017 6:00 PM |  |  |  | 0 |  |  |  | #N/A | #DIV/0! | #DIV/0! | PO | OK
| 7/2/2017 7:00 PM |  |  |  | 0 |  |  |  | #N/A | #DIV/0! | #DIV/0! | PO | OK
| 7/2/2017 8:00 PM | 2 | 1383.64 |  | 1383.64 |  | 60.0357 | 1.9332 | 4 | 9.9162 | 19.1702 | 4.7926 | OK
| 7/2/2017 9:00 PM | 2 | 1366.0787 |  | 1366.0787 |  | 59.5976 | 1.9056 | 4 | 10.0437 | 19.1394 | 4.7848 | OK
| 7/2/2017 10:00 PM | 2 | 1363.0484 |  | 1363.0484 |  | 61.1557 | 1.9401 | 3.8 | 10.0661 | 19.5288 | 5.1392 | OK
| 7/2/2017 11:00 PM | 2 | 1363.4769 |  | 1363.4769 |  | 59.8308 | 1.947 | 4 | 10.0629 | 19.5926 | 4.8982 | OK
| 7/3/2017 12:00 AM | 3 | 1370.8653 |  | 1370.8653 |  | 59.0358 | 1.9469 | 4 | 10.0087 | 19.486 | 4.8715 | OK
| 7/3/2017 1:00 AM | 3 | 1369.7944 |  | 1369.7944 |  | 58.3009 | 1.9263 | 4.4 | 10.0165 | 19.2943 | 4.3851 | OK
| 7/3/2017 2:00 AM | 3 | 1362.5131 |  | 1362.5131 |  | 59.534 | 1.9401 | 4 | 10.07 | 19.5365 | 4.8841 | OK
| 7/3/2017 3:00 AM | 3 | 1361.4422 |  | 1361.4422 |  | 61.6009 | 1.9331 | 3.8 | 10.0779 | 19.4817 | 5.1268 | OK
| 7/3/2017 4:00 AM | 3 | 1356.9449 |  | 1356.9449 |  | 63.4382 | 1.947 | 3.6 | 10.1113 | 19.687 | 5.4686 | OK
| 7/3/2017 5:00 AM | 3 | 1359.1934 |  | 1359.1934 |  | 63.788 | 1.9469 | 3.6 | 10.0946 | 19.6533 | 5.4593 | OK
| 7/3/2017 6:00 AM | 3 | 1360.0501 |  | 1360.0501 |  | 63.8127 | 1.9401 | 3.6 | 10.0882 | 19.5718 | 5.4366 | OK
| 7/3/2017 7:00 AM | 3 | 1354.2679 |  | 1354.2679 |  | 63.5513 | 1.9539 | 3.6 | 10.1313 | 19.7953 | 5.4987 | OK
| 7/3/2017 8:00 AM | 3 | 1351.698 |  | 1351.698 |  | 63.4806 | 1.9745 | 3.6 | 10.1506 | 20.0425 | 5.5674 | OK
| 7/3/2017 9:00 AM | 3 | 1357.2661 |  | 1357.2661 |  | 63.4347 | 1.9814 | 3.6 | 10.1089 | 20.0296 | 5.5638 | OK
| 7/3/2017 10:00 AM | 3 | 1360.0501 |  | 1360.0501 |  | 63.1874 | 1.9745 | 3.6 | 10.0882 | 19.9195 | 5.5332 | OK
| 7/3/2017 11:00 AM | 3 | 1353.6252 |  | 1353.6252 |  | 63.0672 | 1.954 | 3.6 | 10.1361 | 19.8057 | 5.5016 | OK
| 7/3/2017 12:00 PM | 3 | 1358.7652 |  | 1358.7652 |  | 62.8764 | 1.9403 | 3.6 | 10.0978 | 19.5925 | 5.4424 | OK
| 7/3/2017 1:00 PM | 3 | 1367.3316 |  | 1367.3316 |  | 62.4595 | 1.9403 | 3.8 | 10.0345 | 19.4698 | 5.1236 | OK
| 7/3/2017 2:00 PM | 3 | 1361.2281 |  | 1361.2281 |  | 62.0603 | 1.9541 | 3.8 | 10.0795 | 19.6962 | 5.1832 | OK
| 7/3/2017 3:00 PM | 3 | 1350.5201 |  | 1350.5201 |  | 61.4985 | 1.9333 | 3.8 | 10.1594 | 19.6415 | 5.1688 | OK
| 7/3/2017 4:00 PM | 3 | 1364.0123 |  | 1364.0123 |  | 61.4101 | 1.9264 | 3.8 | 10.0589 | 19.3772 | 5.0993 | OK
| 7/3/2017 5:00 PM | 3 | 1362.6522 |  | 1362.6522 |  | 61.8235 | 1.9403 | 3.8 | 10.069 | 19.5366 | 5.1412 | OK
| 7/3/2017 6:00 PM | 3 | 1366.3681 |  | 1366.3681 |  | 60.3749 | 1.9403 | 4 | 10.0416 | 19.4835 | 4.8709 | OK
| 7/3/2017 7:00 PM | 3 | 1361.121 |  | 1361.121 |  | 60.7848 | 1.9403 | 4 | 10.0803 | 19.5586 | 4.8896 | OK
| 7/3/2017 8:00 PM | 3 | 1360.9391 |  | 1360.9391 |  | 60.9296 | 1.9471 | 3.8 | 10.0817 | 19.6303 | 5.1659 | OK
| 7/3/2017 9:00 PM | 3 | 1364.976 |  | 1364.976 |  | 59.3609 | 1.947 | 4 | 10.0518 | 19.5711 | 4.8928 | OK
| 7/3/2017 10:00 PM | 3 | 1362.299 |  | 1362.299 |  | 62.7634 | 1.9469 | 3.6 | 10.0716 | 19.6085 | 5.4468 | OK
| 7/3/2017 11:00 PM | 3 | 1431.8262 |  | 1431.8262 |  | 63.8834 | 1.9469 | 3.6 | 9.5825 | 18.6564 | 5.1823 | OK
| 7/4/2017 12:00 AM | 4 | 1357.052 |  | 1357.052 |  | 64.6925 | 1.9402 | 3.4 | 10.1105 | 19.6162 | 5.7695 | OK
| 7/4/2017 1:00 AM | 4 | 1362.7271 |  | 1362.7271 |  | 65.537 | 1.9402 | 3.4 | 10.0684 | 19.5345 | 5.7454 | OK
| 7/4/2017 2:00 AM | 4 | 1362.7271 |  | 1362.7271 |  | 65.8514 | 1.947 | 3.4 | 10.0684 | 19.6034 | 5.7657 | OK
| 7/4/2017 3:00 AM | 4 | 1362.1918 |  | 1362.1918 |  | 66.0069 | 1.9402 | 3.4 | 10.0724 | 19.5421 | 5.7477 | OK
| 7/4/2017 4:00 AM | 4 | 1360.6928 |  | 1360.6928 |  | 65.756 | 1.9402 | 3.4 | 10.0835 | 19.5637 | 5.754 | OK
| 7/4/2017 5:00 AM | 4 | 1359.515 |  | 1359.515 |  | 61.5479 | 1.947 | 3.8 | 10.0922 | 19.6497 | 5.171 | OK
| 7/4/2017 6:00 AM | 4 | 1349.021 |  | 1349.021 |  | 61.6893 | 1.9332 | 3.8 | 10.1707 | 19.6622 | 5.1743 | OK
| 7/4/2017 7:00 AM | 4 | 1352.9829 |  | 1352.9829 |  | 63.7456 | 1.9882 | 3.6 | 10.1409 | 20.1624 | 5.6007 | OK
| 7/4/2017 8:00 AM | 4 | 1368.6165 |  | 1368.6165 |  | 63.788 | 1.9607 | 3.6 | 10.0251 | 19.6564 | 5.4601 | OK
| 7/4/2017 9:00 AM | 4 | 1365.0831 |  | 1365.0831 |  | 63.7103 | 1.954 | 3.6 | 10.051 | 19.6395 | 5.4554 | OK
| 7/4/2017 10:00 AM | 4 | 1354.482 |  | 1354.482 |  | 63.3958 | 1.9541 | 3.6 | 10.1297 | 19.7943 | 5.4984 | OK
| 7/4/2017 11:00 AM | 4 | 1367.653 |  | 1367.653 |  | 62.9683 | 1.9404 | 3.6 | 10.0322 | 19.4663 | 5.4073 | OK
| 7/4/2017 12:00 PM | 4 | 1354.1608 |  | 1354.1608 |  | 62.509 | 1.899 | 3.8 | 10.1321 | 19.2406 | 5.0633 | OK
| 7/4/2017 1:00 PM | 4 | 1361.9775 |  | 1361.9775 |  | 61.9719 | 1.8716 | 3.8 | 10.074 | 18.8542 | 4.9616 | OK
| 7/4/2017 2:00 PM |  |  |  | 0 |  |  |  | #N/A | #DIV/0! | #DIV/0! | PO | OK
| 7/4/2017 3:00 PM | 4 | 1383.3938 |  | 1383.3938 |  | 61.6539 | 1.892 | 3.8 | 9.918 | 18.765 | 4.9382 | OK
| 7/4/2017 4:00 PM | 4 | 1378.6821 |  | 1378.6821 |  | 61.5727 | 1.8989 | 3.8 | 9.9519 | 18.8973 | 4.973 | OK
| 7/4/2017 5:00 PM | 4 | 1357.4802 |  | 1357.4802 |  | 61.1487 | 1.8841 | 3.8 | 10.1073 | 19.0432 | 5.0114 | OK
| 7/4/2017 6:00 PM | 4 | 1356.3345 |  | 1356.3345 |  | 60.3643 | 1.9194 | 4 | 10.1159 | 19.4165 | 4.8541 | OK
| 7/4/2017 7:00 PM | 4 | 1356.8378 |  | 1356.8378 |  | 59.912 | 1.9128 | 4 | 10.1121 | 19.3422 | 4.8356 | OK
| 7/4/2017 8:00 PM | 4 | 1365.6504 |  | 1365.6504 |  | 61.1275 | 1.9471 | 3.8 | 10.0469 | 19.5625 | 5.148 | OK
| 7/4/2017 9:00 PM | 4 | 1360.4038 |  | 1360.4038 |  | 59.6789 | 1.9333 | 4 | 10.0856 | 19.4988 | 4.8747 | OK
| 7/4/2017 10:00 PM | 4 | 1357.6945 |  | 1357.6945 |  | 60.9543 | 1.954 | 3.8 | 10.1057 | 19.7464 | 5.1964 | OK
| 7/4/2017 11:00 PM | 4 | 1392.0671 |  | 1392.0671 |  | 61.4349 | 1.9539 | 3.8 | 9.8562 | 19.2578 | 5.0678 | OK
| 7/5/2017 12:00 AM | 5 | 1360.5854 |  | 1360.5854 |  | 61.9684 | 1.9402 | 3.8 | 10.0843 | 19.5652 | 5.1487 | OK
| 7/5/2017 1:00 AM | 5 | 1367.3316 |  | 1367.3316 |  | 64.3003 | 1.9402 | 3.6 | 10.0345 | 19.4687 | 5.408 | OK
| 7/5/2017 2:00 AM | 5 | 1358.2299 |  | 1358.2299 |  | 64.6925 | 1.947 | 3.4 | 10.1018 | 19.6683 | 5.7848 | OK
| 7/5/2017 3:00 AM | 5 | 1359.515 |  | 1359.515 |  | 64.6289 | 1.947 | 3.4 | 10.0922 | 19.6497 | 5.7793 | OK
| 7/5/2017 4:00 AM | 5 | 1354.375 |  | 1354.375 |  | 64.5371 | 1.947 | 3.4 | 10.1305 | 19.7243 | 5.8013 | OK
| 7/5/2017 5:00 AM | 5 | 1358.337 |  | 1358.337 |  | 60.336 | 1.9471 | 4 | 10.101 | 19.6679 | 4.917 | OK
| 7/5/2017 6:00 AM | 5 | 1357.6945 |  | 1357.6945 |  | 60.5056 | 1.954 | 4 | 10.1057 | 19.7464 | 4.9366 | OK
| 7/5/2017 7:00 AM | 5 | 1351.4838 |  | 1351.4838 |  | 63.4312 | 2.0019 | 3.6 | 10.1522 | 20.3238 | 5.6455 | OK
| 7/5/2017 8:00 AM | 5 | 1351.5909 |  | 1351.5909 |  | 63.8657 | 1.9952 | 3.6 | 10.1514 | 20.2538 | 5.6261 | OK
| 7/5/2017 9:00 AM | 5 | 1355.7669 |  | 1355.7669 |  | 63.8551 | 1.9607 | 3.6 | 10.1201 | 19.8427 | 5.5119 | OK
| 7/5/2017 10:00 AM | 5 | 1362.9412 |  | 1362.9412 |  | 63.6431 | 1.954 | 3.6 | 10.0668 | 19.6704 | 5.464 | OK
| 7/5/2017 11:00 AM | 5 | 1360.4787 |  | 1360.4787 |  | 63.3499 | 1.9265 | 3.6 | 10.0851 | 19.4286 | 5.3968 | OK
| 7/5/2017 12:00 PM | 5 | 1362.406 |  | 1362.406 |  | 62.933 | 1.961 | 3.6 | 10.0708 | 19.7492 | 5.4859 | OK
| 7/5/2017 1:00 PM | 5 | 1339.8122 |  | 1339.8122 |  | 62.622 | 1.9748 | 3.6 | 10.2406 | 20.2236 | 5.6177 | OK
| 7/5/2017 2:00 PM | 5 | 1357.9086 |  | 1357.9086 |  | 62.2298 | 1.9817 | 3.8 | 10.1042 | 20.0233 | 5.2693 | OK
| 7/5/2017 3:00 PM | 5 | 1349.16 |  | 1349.16 |  | 61.5762 | 1.9954 | 3.8 | 10.1697 | 20.2925 | 5.3401 | OK
| 7/5/2017 4:00 PM | 5 | 1158.4507 |  | 1158.4507 |  | 61.2476 | 1.961 | 3.8 | 11.8439 | 23.2262 | 6.1122 | OK
| 7/5/2017 5:00 PM |  |  |  | 0 |  |  |  | #N/A | #DIV/0! | #DIV/0! | PO | OK
| 7/5/2017 6:00 PM |  |  |  | 0 |  |  |  | #N/A | #DIV/0! | #DIV/0! | PO | OK
| 7/5/2017 7:00 PM |  |  |  | 0 |  |  |  | #N/A | #DIV/0! | #DIV/0! | PO | OK
| 7/5/2017 8:00 PM |  |  |  | 0 |  |  |  | #N/A | #DIV/0! | #DIV/0! | PO | OK
| 7/5/2017 9:00 PM |  |  |  | 0 |  |  |  | #N/A | #DIV/0! | #DIV/0! | PO | OK
| 7/5/2017 10:00 PM |  |  |  | 0 |  |  |  | #N/A | #DIV/0! | #DIV/0! | PO | OK
| 7/5/2017 11:00 PM |  |  |  | 0 |  |  |  | #N/A | #DIV/0! | #DIV/0! | PO | OK
| 7/6/2017 12:00 AM |  |  |  | 0 |  |  |  | #N/A | #DIV/0! | #DIV/0! | PO | OK
| 7/6/2017 1:00 AM |  |  |  | 0 |  |  |  | #N/A | #DIV/0! | #DIV/0! | PO | OK
| 7/6/2017 2:00 AM |  |  |  | 0 |  |  |  | #N/A | #DIV/0! | #DIV/0! | PO | OK
| 7/6/2017 3:00 AM |  |  |  | 0 |  |  |  | #N/A | #DIV/0! | #DIV/0! | PO | OK
| 7/6/2017 4:00 AM |  |  |  | 0 |  |  |  | #N/A | #DIV/0! | #DIV/0! | PO | OK
| 7/6/2017 5:00 AM |  |  |  | 0 |  |  |  | #N/A | #DIV/0! | #DIV/0! | PO | OK
| 7/6/2017 6:00 AM |  |  |  | 0 |  |  |  | #N/A | #DIV/0! | #DIV/0! | PO | OK
| 7/6/2017 7:00 AM |  |  |  | 0 |  |  |  | #N/A | #DIV/0! | #DIV/0! | PO | OK
| 7/6/2017 8:00 AM |  |  |  | 0 |  |  |  | #N/A | #DIV/0! | #DIV/0! | PO | OK
| 7/6/2017 9:00 AM |  |  |  | 0 |  |  |  | #N/A | #DIV/0! | #DIV/0! | PO | OK
| 7/6/2017 10:00 AM |  |  |  | 0 |  |  |  | #N/A | #DIV/0! | #DIV/0! | PO | OK
| 7/6/2017 11:00 AM |  |  |  | 0 |  |  |  | #N/A | #DIV/0! | #DIV/0! | PO | OK
| 7/6/2017 12:00 PM |  |  |  | 0 |  |  |  | #N/A | #DIV/0! | #DIV/0! | PO | OK
| 7/6/2017 1:00 PM |  |  |  | 0 |  |  |  | #N/A | #DIV/0! | #DIV/0! | PO | OK
| 7/6/2017 2:00 PM |  |  |  | 0 |  |  |  | #N/A | #DIV/0! | #DIV/0! | PO | OK
| 7/6/2017 3:00 PM |  |  |  | 0 |  |  |  | #N/A | #DIV/0! | #DIV/0! | PO | OK
| 7/6/2017 4:00 PM |  |  |  | 0 |  |  |  | #N/A | #DIV/0! | #DIV/0! | PO | OK
| 7/6/2017 5:00 PM |  |  |  | 0 |  |  |  | #N/A | #DIV/0! | #DIV/0! | PO | OK
| 7/6/2017 6:00 PM |  |  |  | 0 |  |  |  | #N/A | #DIV/0! | #DIV/0! | PO | OK
| 7/6/2017 7:00 PM |  |  |  | 0 |  |  |  | #N/A | #DIV/0! | #DIV/0! | PO | OK
| 7/6/2017 8:00 PM |  |  |  | 0 |  |  |  | #N/A | #DIV/0! | #DIV/0! | PO | OK
| 7/6/2017 9:00 PM |  |  |  | 0 |  |  |  | #N/A | #DIV/0! | #DIV/0! | PO | OK
| 7/6/2017 10:00 PM |  |  |  | 0 |  |  |  | #N/A | #DIV/0! | #DIV/0! | PO | OK
| 7/6/2017 11:00 PM |  |  |  | 0 |  |  |  | #N/A | #DIV/0! | #DIV/0! | PO | OK
| 7/7/2017 12:00 AM |  |  |  | 0 |  |  |  | #N/A | #DIV/0! | #DIV/0! | PO | OK
| 7/7/2017 1:00 AM |  |  |  | 0 |  |  |  | #N/A | #DIV/0! | #DIV/0! | PO | OK
| 7/7/2017 2:00 AM |  |  |  | 0 |  |  |  | #N/A | #DIV/0! | #DIV/0! | PO | OK
| 7/7/2017 3:00 AM |  |  |  | 0 |  |  |  | #N/A | #DIV/0! | #DIV/0! | PO | OK
| 7/7/2017 4:00 AM |  |  |  | 0 |  |  |  | #N/A | #DIV/0! | #DIV/0! | PO | OK
| 7/7/2017 5:00 AM |  |  |  | 0 |  |  |  | #N/A | #DIV/0! | #DIV/0! | PO | OK
| 7/7/2017 6:00 AM |  |  |  | 0 |  |  |  | #N/A | #DIV/0! | #DIV/0! | PO | OK
| 7/7/2017 7:00 AM |  |  |  | 0 |  |  |  | #N/A | #DIV/0! | #DIV/0! | PO | OK
| 7/7/2017 8:00 AM |  |  |  | 0 |  |  |  | #N/A | #DIV/0! | #DIV/0! | PO | OK
| 7/7/2017 9:00 AM |  |  |  | 0 |  |  |  | #N/A | #DIV/0! | #DIV/0! | PO | OK
| 7/7/2017 10:00 AM |  |  |  | 0 |  |  |  | #N/A | #DIV/0! | #DIV/0! | PO | OK
| 7/7/2017 11:00 AM |  |  |  | 0 |  |  |  | #N/A | #DIV/0! | #DIV/0! | PO | OK
| 7/7/2017 12:00 PM |  |  |  | 0 |  |  |  | #N/A | #DIV/0! | #DIV/0! | PO | OK
| 7/7/2017 1:00 PM |  |  |  | 0 |  |  |  | #N/A | #DIV/0! | #DIV/0! | PO | OK
| 7/7/2017 2:00 PM |  |  |  | 0 |  |  |  | #N/A | #DIV/0! | #DIV/0! | PO | OK
| 7/7/2017 3:00 PM |  |  |  | 0 |  |  |  | #N/A | #DIV/0! | #DIV/0! | PO | OK
| 7/7/2017 4:00 PM |  |  |  | 0 |  |  |  | #N/A | #DIV/0! | #DIV/0! | PO | OK
| 7/7/2017 5:00 PM |  |  |  | 0 |  |  |  | #N/A | #DIV/0! | #DIV/0! | PO | OK
| 7/7/2017 6:00 PM |  |  |  | 0 |  |  |  | #N/A | #DIV/0! | #DIV/0! | PO | OK
| 7/7/2017 7:00 PM |  |  |  | 0 |  |  |  | #N/A | #DIV/0! | #DIV/0! | PO | OK
| 7/7/2017 8:00 PM |  |  |  | 0 |  |  |  | #N/A | #DIV/0! | #DIV/0! | PO | OK
| 7/7/2017 9:00 PM |  |  |  | 0 |  |  |  | #N/A | #DIV/0! | #DIV/0! | PO | OK
| 7/7/2017 10:00 PM |  |  |  | 0 |  |  |  | #N/A | #DIV/0! | #DIV/0! | PO | OK
| 7/7/2017 11:00 PM |  |  |  | 0 |  |  |  | #N/A | #DIV/0! | #DIV/0! | PO | OK
| 7/8/2017 12:00 AM |  |  |  | 0 |  |  |  | #N/A | #DIV/0! | #DIV/0! | PO | OK
| 7/8/2017 1:00 AM |  |  |  | 0 |  |  |  | #N/A | #DIV/0! | #DIV/0! | PO | OK
| 7/8/2017 2:00 AM |  |  |  | 0 |  |  |  | #N/A | #DIV/0! | #DIV/0! | PO | OK
| 7/8/2017 3:00 AM |  |  |  | 0 |  |  |  | #N/A | #DIV/0! | #DIV/0! | PO | OK
| 7/8/2017 4:00 AM |  |  |  | 0 |  |  |  | #N/A | #DIV/0! | #DIV/0! | PO | OK
| 7/8/2017 5:00 AM |  |  |  | 0 |  |  |  | #N/A | #DIV/0! | #DIV/0! | PO | OK
| 7/8/2017 6:00 AM |  |  |  | 0 |  |  |  | #N/A | #DIV/0! | #DIV/0! | PO | OK
| 7/8/2017 7:00 AM |  |  |  | 0 |  |  |  | #N/A | #DIV/0! | #DIV/0! | PO | OK
| 7/8/2017 8:00 AM |  |  |  | 0 |  |  |  | #N/A | #DIV/0! | #DIV/0! | PO | OK
| 7/8/2017 9:00 AM |  |  |  | 0 |  |  |  | #N/A | #DIV/0! | #DIV/0! | PO | OK
| 7/8/2017 10:00 AM |  |  |  | 0 |  |  |  | #N/A | #DIV/0! | #DIV/0! | PO | OK
| 7/8/2017 11:00 AM |  |  |  | 0 |  |  |  | #N/A | #DIV/0! | #DIV/0! | PO | OK
| 7/8/2017 12:00 PM |  |  |  | 0 |  |  |  | #N/A | #DIV/0! | #DIV/0! | PO | OK
| 7/8/2017 1:00 PM |  |  |  | 0 |  |  |  | #N/A | #DIV/0! | #DIV/0! | PO | OK
| 7/8/2017 2:00 PM |  |  |  | 0 |  |  |  | #N/A | #DIV/0! | #DIV/0! | PO | OK
| 7/8/2017 3:00 PM |  |  |  | 0 |  |  |  | #N/A | #DIV/0! | #DIV/0! | PO | OK
| 7/8/2017 4:00 PM |  |  |  | 0 |  |  |  | #N/A | #DIV/0! | #DIV/0! | PO | OK
| 7/8/2017 5:00 PM |  |  |  | 0 |  |  |  | #N/A | #DIV/0! | #DIV/0! | PO | OK
| 7/8/2017 6:00 PM |  |  |  | 0 |  |  |  | #N/A | #DIV/0! | #DIV/0! | PO | OK
| 7/8/2017 7:00 PM |  |  |  | 0 |  |  |  | #N/A | #DIV/0! | #DIV/0! | PO | OK
| 7/8/2017 8:00 PM |  |  |  | 0 |  |  |  | #N/A | #DIV/0! | #DIV/0! | PO | OK
| 7/8/2017 9:00 PM |  |  |  | 0 |  |  |  | #N/A | #DIV/0! | #DIV/0! | PO | OK
| 7/8/2017 10:00 PM |  |  |  | 0 |  |  |  | #N/A | #DIV/0! | #DIV/0! | PO | OK
| 7/8/2017 11:00 PM |  |  |  | 0 |  |  |  | #N/A | #DIV/0! | #DIV/0! | PO | OK
| 7/9/2017 12:00 AM |  |  |  | 0 |  |  |  | #N/A | #DIV/0! | #DIV/0! | PO | OK
| 7/9/2017 1:00 AM |  |  |  | 0 |  |  |  | #N/A | #DIV/0! | #DIV/0! | PO | OK
| 7/9/2017 2:00 AM |  |  |  | 0 |  |  |  | #N/A | #DIV/0! | #DIV/0! | PO | OK
| 7/9/2017 3:00 AM |  |  |  | 0 |  |  |  | #N/A | #DIV/0! | #DIV/0! | PO | OK
| 7/9/2017 4:00 AM |  |  |  | 0 |  |  |  | #N/A | #DIV/0! | #DIV/0! | PO | OK
| 7/9/2017 5:00 AM |  |  |  | 0 |  |  |  | #N/A | #DIV/0! | #DIV/0! | PO | OK
| 7/9/2017 6:00 AM |  |  |  | 0 |  |  |  | #N/A | #DIV/0! | #DIV/0! | PO | OK
| 7/9/2017 7:00 AM |  |  |  | 0 |  |  |  | #N/A | #DIV/0! | #DIV/0! | PO | OK
| 7/9/2017 8:00 AM |  |  |  | 0 |  |  |  | #N/A | #DIV/0! | #DIV/0! | PO | OK
| 7/9/2017 9:00 AM |  |  |  | 0 |  |  |  | #N/A | #DIV/0! | #DIV/0! | PO | OK
| 7/9/2017 10:00 AM |  |  |  | 0 |  |  |  | #N/A | #DIV/0! | #DIV/0! | PO | OK
| 7/9/2017 11:00 AM |  |  |  | 0 |  |  |  | #N/A | #DIV/0! | #DIV/0! | PO | OK
| 7/9/2017 12:00 PM |  |  |  | 0 |  |  |  | #N/A | #DIV/0! | #DIV/0! | PO | OK
| 7/9/2017 1:00 PM |  |  |  | 0 |  |  |  | #N/A | #DIV/0! | #DIV/0! | PO | OK
| 7/9/2017 2:00 PM |  |  |  | 0 |  |  |  | #N/A | #DIV/0! | #DIV/0! | PO | OK
| 7/9/2017 3:00 PM |  |  |  | 0 |  |  |  | #N/A | #DIV/0! | #DIV/0! | PO | OK
| 7/9/2017 4:00 PM |  |  |  | 0 |  |  |  | #N/A | #DIV/0! | #DIV/0! | PO | OK
| 7/9/2017 5:00 PM |  |  |  | 0 |  |  |  | #N/A | #DIV/0! | #DIV/0! | PO | OK
| 7/9/2017 6:00 PM |  |  |  | 0 |  |  |  | #N/A | #DIV/0! | #DIV/0! | PO | OK
| 7/9/2017 7:00 PM |  |  |  | 0 |  |  |  | #N/A | #DIV/0! | #DIV/0! | PO | OK
| 7/9/2017 8:00 PM |  |  |  | 0 |  |  |  | #N/A | #DIV/0! | #DIV/0! | PO | OK
| 7/9/2017 9:00 PM |  |  |  | 0 |  |  |  | #N/A | #DIV/0! | #DIV/0! | PO | OK
| 7/9/2017 10:00 PM |  |  |  | 0 |  |  |  | #N/A | #DIV/0! | #DIV/0! | PO | OK
| 7/9/2017 11:00 PM |  |  |  | 0 |  |  |  | #N/A | #DIV/0! | #DIV/0! | PO | OK
| 7/10/2017 12:00 AM |  |  |  | 0 |  |  |  | #N/A | #DIV/0! | #DIV/0! | PO | OK
| 7/10/2017 1:00 AM |  |  |  | 0 |  |  |  | #N/A | #DIV/0! | #DIV/0! | PO | OK
| 7/10/2017 2:00 AM |  |  |  | 0 |  |  |  | #N/A | #DIV/0! | #DIV/0! | PO | OK
| 7/10/2017 3:00 AM |  |  |  | 0 |  |  |  | #N/A | #DIV/0! | #DIV/0! | PO | OK
| 7/10/2017 4:00 AM |  |  |  | 0 |  |  |  | #N/A | #DIV/0! | #DIV/0! | PO | OK
| 7/10/2017 5:00 AM |  |  |  | 0 |  |  |  | #N/A | #DIV/0! | #DIV/0! | PO | OK
| 7/10/2017 6:00 AM |  |  |  | 0 |  |  |  | #N/A | #DIV/0! | #DIV/0! | PO | OK
| 7/10/2017 7:00 AM |  |  |  | 0 |  |  |  | #N/A | #DIV/0! | #DIV/0! | PO | OK
| 7/10/2017 8:00 AM |  |  |  | 0 |  |  |  | #N/A | #DIV/0! | #DIV/0! | PO | OK
| 7/10/2017 9:00 AM |  |  |  | 0 |  |  |  | #N/A | #DIV/0! | #DIV/0! | PO | OK
| 7/10/2017 10:00 AM |  |  |  | 0 |  |  |  | #N/A | #DIV/0! | #DIV/0! | PO | OK
| 7/10/2017 11:00 AM |  |  |  | 0 |  |  |  | #N/A | #DIV/0! | #DIV/0! | PO | OK
| 7/10/2017 12:00 PM |  |  |  | 0 |  |  |  | #N/A | #DIV/0! | #DIV/0! | PO | OK
| 7/10/2017 1:00 PM |  |  |  | 0 |  |  |  | #N/A | #DIV/0! | #DIV/0! | PO | OK
| 7/10/2017 2:00 PM |  |  |  | 0 |  |  |  | #N/A | #DIV/0! | #DIV/0! | PO | OK
| 7/10/2017 3:00 PM |  |  |  | 0 |  |  |  | #N/A | #DIV/0! | #DIV/0! | PO | OK
| 7/10/2017 4:00 PM |  |  |  | 0 |  |  |  | #N/A | #DIV/0! | #DIV/0! | PO | OK
| 7/10/2017 5:00 PM |  |  |  | 0 |  |  |  | #N/A | #DIV/0! | #DIV/0! | PO | OK
| 7/10/2017 6:00 PM |  |  |  | 0 |  |  |  | #N/A | #DIV/0! | #DIV/0! | PO | OK
| 7/10/2017 7:00 PM |  |  |  | 0 |  |  |  | #N/A | #DIV/0! | #DIV/0! | PO | OK
| 7/10/2017 8:00 PM |  |  |  | 0 |  |  |  | #N/A | #DIV/0! | #DIV/0! | PO | OK
| 7/10/2017 9:00 PM |  |  |  | 0 |  |  |  | #N/A | #DIV/0! | #DIV/0! | PO | OK
| 7/10/2017 10:00 PM |  |  |  | 0 |  |  |  | #N/A | #DIV/0! | #DIV/0! | PO | OK
| 7/10/2017 11:00 PM |  |  |  | 0 |  |  |  | #N/A | #DIV/0! | #DIV/0! | PO | OK
| 7/11/2017 12:00 AM |  |  |  | 0 |  |  |  | #N/A | #DIV/0! | #DIV/0! | PO | OK
| 7/11/2017 1:00 AM |  |  |  | 0 |  |  |  | #N/A | #DIV/0! | #DIV/0! | PO | OK
| 7/11/2017 2:00 AM |  |  |  | 0 |  |  |  | #N/A | #DIV/0! | #DIV/0! | PO | OK
| 7/11/2017 3:00 AM |  |  |  | 0 |  |  |  | #N/A | #DIV/0! | #DIV/0! | PO | OK
| 7/11/2017 4:00 AM |  |  |  | 0 |  |  |  | #N/A | #DIV/0! | #DIV/0! | PO | OK
| 7/11/2017 5:00 AM |  |  |  | 0 |  |  |  | #N/A | #DIV/0! | #DIV/0! | PO | OK
| 7/11/2017 6:00 AM |  |  |  | 0 |  |  |  | #N/A | #DIV/0! | #DIV/0! | PO | OK
| 7/11/2017 7:00 AM |  |  |  | 0 |  |  |  | #N/A | #DIV/0! | #DIV/0! | PO | OK
| 7/11/2017 8:00 AM |  |  |  | 0 |  |  |  | #N/A | #DIV/0! | #DIV/0! | PO | OK
| 7/11/2017 9:00 AM | 11 | 1135.7172 |  | 1135.7172 |  | 65.1624 | 2.208 | 3.4 | 12.0809 | 26.675 | 7.8456 | OK
| 7/11/2017 10:00 AM |  |  |  | 0 |  |  |  | #N/A | #DIV/0! | #DIV/0! | PO | OK
| 7/11/2017 11:00 AM | 11 | 1498.6867 |  | 1498.6867 |  | 61.5303 | 2.1945 | 3.8 | 9.155 | 20.0911 | 5.2871 | OK
| 7/11/2017 12:00 PM | 11 | 1503.6447 |  | 1503.6447 |  | 61.7105 | 2.2083 | 3.8 | 9.1248 | 20.1508 | 5.3028 | OK
| 7/11/2017 1:00 PM |  |  |  | 0 |  |  |  | #N/A | #DIV/0! | #DIV/0! | PO | OK
| 7/11/2017 2:00 PM |  |  |  | 0 |  |  |  | #N/A | #DIV/0! | #DIV/0! | PO | OK
| 7/11/2017 3:00 PM |  |  |  | 0 |  |  |  | #N/A | #DIV/0! | #DIV/0! | PO | OK
| 7/11/2017 4:00 PM |  |  |  | 0 |  |  |  | #N/A | #DIV/0! | #DIV/0! | PO | OK
| 7/11/2017 5:00 PM |  |  |  | 0 |  |  |  | #N/A | #DIV/0! | #DIV/0! | PO | OK
| 7/11/2017 6:00 PM |  |  |  | 0 |  |  |  | #N/A | #DIV/0! | #DIV/0! | PO | OK
| 7/11/2017 7:00 PM |  |  |  | 0 |  |  |  | #N/A | #DIV/0! | #DIV/0! | PO | OK
| 7/11/2017 8:00 PM |  |  |  | 0 |  |  |  | #N/A | #DIV/0! | #DIV/0! | PO | OK
| 7/11/2017 9:00 PM |  |  |  | 0 |  |  |  | #N/A | #DIV/0! | #DIV/0! | PO | OK
| 7/11/2017 10:00 PM |  |  |  | 0 |  |  |  | #N/A | #DIV/0! | #DIV/0! | PO | OK
| 7/11/2017 11:00 PM |  |  |  | 0 |  |  |  | #N/A | #DIV/0! | #DIV/0! | PO | OK
| 7/12/2017 12:00 AM |  |  |  | 0 |  |  |  | #N/A | #DIV/0! | #DIV/0! | PO | OK
| 7/12/2017 1:00 AM |  |  |  | 0 |  |  |  | #N/A | #DIV/0! | #DIV/0! | PO | OK
| 7/12/2017 2:00 AM |  |  |  | 0 |  |  |  | #N/A | #DIV/0! | #DIV/0! | PO | OK
| 7/12/2017 3:00 AM |  |  |  | 0 |  |  |  | #N/A | #DIV/0! | #DIV/0! | PO | OK
| 7/12/2017 4:00 AM |  |  |  | 0 |  |  |  | #N/A | #DIV/0! | #DIV/0! | PO | OK
| 7/12/2017 5:00 AM |  |  |  | 0 |  |  |  | #N/A | #DIV/0! | #DIV/0! | PO | OK
| 7/12/2017 6:00 AM |  |  |  | 0 |  |  |  | #N/A | #DIV/0! | #DIV/0! | PO | OK
| 7/12/2017 7:00 AM |  |  |  | 0 |  |  |  | #N/A | #DIV/0! | #DIV/0! | PO | OK
| 7/12/2017 8:00 AM | 12 | 1018.5394 |  | 1018.5394 |  | 61.9613 | 2.4212 | 3.8 | 13.4708 | 32.6154 | 8.583 | OK
| 7/12/2017 9:00 AM | 12 | 899.4664 |  | 899.4664 |  | 61.6433 | 2.2497 | 3.8 | 15.2541 | 34.3164 | 9.0306 | OK
| 7/12/2017 10:00 AM | 12 | 1748.0764 |  | 1748.0764 |  | 61.7493 | 2.2153 | 3.8 | 7.8489 | 17.3877 | 4.5757 | OK
| 7/12/2017 11:00 AM | 12 | 2128.5321 |  | 2128.5321 |  | 62.0073 | 1.975 | 3.8 | 6.446 | 12.7305 | 3.3501 | OK
| 7/12/2017 12:00 PM | 12 | 2165.3681 |  | 2165.3681 |  | 61.5691 | 2.0847 | 3.8 | 6.3363 | 13.2097 | 3.4762 | OK
| 7/12/2017 1:00 PM | 12 | 2160.1533 |  | 2160.1533 |  | 61.3218 | 2.0643 | 3.8 | 6.3516 | 13.1117 | 3.4505 | OK
| 7/12/2017 2:00 PM | 12 | 2067.7108 |  | 2067.7108 |  | 61.9684 | 2.0644 | 3.8 | 6.6356 | 13.6986 | 3.6049 | OK
| 7/12/2017 3:00 PM | 12 | 2052.6445 |  | 2052.6445 |  | 62.4489 | 2.0644 | 3.8 | 6.6843 | 13.7992 | 3.6314 | OK
| 7/12/2017 4:00 PM | 12 | 2098.0466 |  | 2098.0466 |  | 62.4913 | 2.0233 | 3.8 | 6.5397 | 13.2318 | 3.4821 | OK
| 7/12/2017 5:00 PM | 12 | 990.4096 |  | 990.4096 |  | 61.6221 | 1.8996 | 3.8 | 13.8534 | 26.3161 | 6.9253 | OK
| 7/12/2017 6:00 PM |  |  |  | 0 |  |  |  | #N/A | #DIV/0! | #DIV/0! | PO | OK
| 7/12/2017 7:00 PM | 12 | 992.337 |  | 992.337 |  | 60.6434 | 2.0093 | 4 | 13.8265 | 27.7815 | 6.9454 | OK
| 7/12/2017 8:00 PM | 12 | 945.3289 |  | 945.3289 |  | 60.7954 | 1.9956 | 4 | 14.514 | 28.9642 | 7.2411 | OK
| 7/12/2017 9:00 PM | 12 | 943.0801 |  | 943.0801 |  | 60.011 | 2.0023 | 4 | 14.5486 | 29.1314 | 7.2828 | OK
| 7/12/2017 10:00 PM | 12 | 931.6226 |  | 931.6226 |  | 59.8025 | 2.0022 | 4 | 14.7275 | 29.4881 | 7.372 | OK
| 7/12/2017 11:00 PM | 12 | 951.1112 |  | 951.1112 |  | 59.5799 | 1.9955 | 4 | 14.4258 | 28.7866 | 7.1966 | OK
| 7/13/2017 12:00 AM | 13 | 946.0463 |  | 946.0463 |  | 60.8907 | 1.9818 | 3.8 | 14.503 | 28.7421 | 7.5637 | OK
| 7/13/2017 1:00 AM | 13 | 944.4721 |  | 944.4721 |  | 62.8623 | 1.968 | 3.6 | 14.5272 | 28.5894 | 7.9415 | OK
| 7/13/2017 2:00 AM | 13 | 953.4669 |  | 953.4669 |  | 63.9823 | 1.9542 | 3.6 | 14.3901 | 28.1211 | 7.8114 | OK
| 7/13/2017 3:00 AM | 13 | 1758.5703 |  | 1758.5703 |  | 65.2932 | 1.961 | 3.4 | 7.8021 | 15.3002 | 4.5001 | OK
| 7/13/2017 4:00 AM | 13 | 1729.9799 |  | 1729.9799 |  | 65.2649 | 1.9336 | 3.4 | 7.931 | 15.3358 | 4.5105 | OK
| 7/13/2017 5:00 AM | 13 | 1763.8496 |  | 1763.8496 |  | 65.3214 | 1.7273 | 3.4 | 7.7787 | 13.4364 | 3.9519 | OK
| 7/13/2017 6:00 AM | 13 | 1767.1367 |  | 1767.1367 |  | 62.1769 | 1.8855 | 3.8 | 7.7643 | 14.6394 | 3.8525 | OK
| 7/13/2017 7:00 AM | 13 | 1467.4195 |  | 1467.4195 |  | 63.0566 | 2.016 | 3.6 | 9.3501 | 18.8502 | 5.2362 | OK
| 7/13/2017 8:00 AM | 13 | 1442.1807 |  | 1442.1807 |  | 63.4453 | 2.0984 | 3.6 | 9.5137 | 19.964 | 5.5456 | OK
| 7/13/2017 9:00 AM | 13 | 1441.6129 |  | 1441.6129 |  | 63.8269 | 2.0572 | 3.6 | 9.5175 | 19.5798 | 5.4388 | OK
| 7/13/2017 10:00 AM | 13 | 1452.9958 |  | 1452.9958 |  | 63.4877 | 2.0642 | 3.6 | 9.4429 | 19.4921 | 5.4145 | OK
| 7/13/2017 11:00 AM | 13 | 1465.8133 |  | 1465.8133 |  | 63.2969 | 2.071 | 3.6 | 9.3603 | 19.3857 | 5.3849 | OK
| 7/13/2017 12:00 PM | 13 | 1472.9127 |  | 1472.9127 |  | 62.463 | 2.0428 | 3.8 | 9.3152 | 19.0291 | 5.0077 | OK
| 7/13/2017 1:00 PM | 13 | 1449.2479 |  | 1449.2479 |  | 62.4595 | 2.0301 | 3.8 | 9.4673 | 19.2193 | 5.0577 | OK
| 7/13/2017 2:00 PM | 13 | 1447.5347 |  | 1447.5347 |  | 61.7776 | 2.044 | 3.8 | 9.4785 | 19.3739 | 5.0984 | OK
| 7/13/2017 3:00 PM | 13 | 1440.4675 |  | 1440.4675 |  | 61.2299 | 2.0028 | 3.8 | 9.525 | 19.0765 | 5.0201 | OK
| 7/13/2017 4:00 PM | 13 | 1457.4931 |  | 1457.4931 |  | 61.0321 | 2.0302 | 3.8 | 9.4138 | 19.1116 | 5.0294 | OK
| 7/13/2017 5:00 PM | 13 | 1453.103 |  | 1453.103 |  | 60.1276 | 2.0439 | 4 | 9.4422 | 19.2986 | 4.8247 | OK
| 7/13/2017 6:00 PM | 13 | 1448.3916 |  | 1448.3916 |  | 59.5517 | 2.0439 | 4 | 9.4729 | 19.3614 | 4.8404 | OK
| 7/13/2017 7:00 PM | 13 | 1470.3427 |  | 1470.3427 |  | 61.8271 | 2.0231 | 3.8 | 9.3315 | 18.8786 | 4.9681 | OK
| 7/13/2017 8:00 PM | 13 | 1440.6816 |  | 1440.6816 |  | 60.6222 | 1.8374 | 4 | 9.5236 | 17.4991 | 4.3748 | OK
| 7/13/2017 9:00 PM | 13 | 1449.3551 |  | 1449.3551 |  | 59.8555 | 2.0231 | 4 | 9.4666 | 19.152 | 4.788 | OK
| 7/13/2017 10:00 PM | 13 | 1434.5778 |  | 1434.5778 |  | 62.1415 | 2.0368 | 3.8 | 9.5641 | 19.4803 | 5.1264 | OK
| 7/13/2017 11:00 PM | 13 | 1454.8161 |  | 1454.8161 |  | 63.7173 | 2.0298 | 3.6 | 9.4311 | 19.1437 | 5.3177 | OK
| 7/14/2017 12:00 AM | 14 | 1445.3929 |  | 1445.3929 |  | 64.1731 | 2.0438 | 3.6 | 9.4926 | 19.4006 | 5.389 | OK
| 7/14/2017 1:00 AM | 14 | 1438.6472 |  | 1438.6472 |  | 64.5724 | 2.0437 | 3.4 | 9.5371 | 19.4905 | 5.7325 | OK
| 7/14/2017 2:00 AM | 14 | 1454.3879 |  | 1454.3879 |  | 63.8057 | 2.0504 | 3.6 | 9.4339 | 19.3432 | 5.3731 | OK
| 7/14/2017 3:00 AM | 14 | 1444.0009 |  | 1444.0009 |  | 65.3674 | 1.9681 | 3.4 | 9.5017 | 18.7004 | 5.5001 | OK
| 7/14/2017 4:00 AM | 14 | 1449.2479 |  | 1449.2479 |  | 66.3567 | 2.0572 | 3.2 | 9.4673 | 19.4766 | 6.0864 | OK
| 7/14/2017 5:00 AM | 14 | 1441.4312 |  | 1441.4312 |  | 64.4805 | 2.0642 | 3.4 | 9.5187 | 19.6484 | 5.779 | OK
| 7/14/2017 6:00 AM | 14 | 1855.9063 |  | 1855.9063 |  | 61.8977 | 2.1192 | 3.8 | 7.3929 | 15.667 | 4.1229 | OK
| 7/14/2017 7:00 AM | 14 | 1868.7559 |  | 1868.7559 |  | 62.0709 | 2.0847 | 3.8 | 7.3421 | 15.3063 | 4.028 | OK
| 7/14/2017 8:00 AM | 14 | 1845.4122 |  | 1845.4122 |  | 63.735 | 2.1192 | 3.6 | 7.4349 | 15.7561 | 4.3767 | OK
| 7/14/2017 9:00 AM | 14 | 1843.5172 |  | 1843.5172 |  | 64.0954 | 2.0986 | 3.6 | 7.4426 | 15.6186 | 4.3385 | OK
| 7/14/2017 10:00 AM | 14 | 1839.9512 |  | 1839.9512 |  | 63.6785 | 2.0505 | 3.6 | 7.457 | 15.2906 | 4.2474 | OK
| 7/14/2017 11:00 AM | 14 | 1846.4832 |  | 1846.4832 |  | 63.3428 | 2.0438 | 3.6 | 7.4306 | 15.1864 | 4.2184 | OK
| 7/14/2017 12:00 PM | 14 | 1820.6018 |  | 1820.6018 |  | 63.788 | 2.0505 | 3.6 | 7.5363 | 15.4531 | 4.2925 | OK
| 7/14/2017 1:00 PM | 14 | 1855.7243 |  | 1855.7243 |  | 64.7915 | 2.0849 | 3.4 | 7.3936 | 15.4146 | 4.5337 | OK
| 7/14/2017 2:00 PM | 14 | 1829.7038 |  | 1829.7038 |  | 64.7066 | 2.0643 | 3.4 | 7.4988 | 15.4797 | 4.5529 | OK
| 7/14/2017 3:00 PM | 14 | 1853.4755 |  | 1853.4755 |  | 62.3994 | 2.0712 | 3.8 | 7.4026 | 15.3319 | 4.0347 | OK
| 7/14/2017 4:00 PM | 14 | 1829.7038 |  | 1829.7038 |  | 61.8377 | 2.0918 | 3.8 | 7.4988 | 15.686 | 4.1279 | OK
| 7/14/2017 5:00 PM | 14 | 1851.1197 |  | 1851.1197 |  | 59.8838 | 2.1056 | 4 | 7.412 | 15.6068 | 3.9017 | OK
| 7/14/2017 6:00 PM | 14 | 1818.2462 |  | 1818.2462 |  | 59.5057 | 2.0849 | 4 | 7.546 | 15.7323 | 3.9331 | OK
| 7/14/2017 7:00 PM | 14 | 1864.2907 |  | 1864.2907 |  | 60.7106 | 2.0986 | 4 | 7.3596 | 15.4446 | 3.8611 | OK
| 7/14/2017 8:00 PM | 14 | 1846.4083 |  | 1846.4083 |  | 62.7634 | 2.0779 | 3.6 | 7.4309 | 15.4407 | 4.2891 | OK
| 7/14/2017 9:00 PM | 14 | 1841.6965 |  | 1841.6965 |  | 63.4771 | 2.0917 | 3.6 | 7.4499 | 15.583 | 4.3286 | OK
| 7/14/2017 10:00 PM | 14 | 1838.8806 |  | 1838.8806 |  | 63.7527 | 2.0917 | 3.6 | 7.4613 | 15.6069 | 4.3353 | OK
| 7/14/2017 11:00 PM | 14 | 1841.8039 |  | 1841.8039 |  | 64.5088 | 2.0984 | 3.4 | 7.4495 | 15.6324 | 4.5978 | OK
| 7/15/2017 12:00 AM | 15 | 1860.3287 |  | 1860.3287 |  | 64.7879 | 2.0916 | 3.4 | 7.3753 | 15.4262 | 4.5371 | OK
| 7/15/2017 1:00 AM | 15 | 1835.8072 |  | 1835.8072 |  | 65.3497 | 2.0916 | 3.4 | 7.4738 | 15.6322 | 4.5977 | OK
| 7/15/2017 2:00 AM | 15 | 1858.2943 |  | 1858.2943 |  | 66.3531 | 2.0779 | 3.2 | 7.3834 | 15.3419 | 4.7944 | OK
| 7/15/2017 3:00 AM | 15 | 1824.9601 |  | 1824.9601 |  | 62.4136 | 2.0916 | 3.8 | 7.5183 | 15.7251 | 4.1382 | OK
| 7/15/2017 4:00 AM | 15 | 1898.5562 |  | 1898.5562 |  | 61.8907 | 2.0986 | 3.8 | 7.2268 | 15.1658 | 3.991 | OK
| 7/15/2017 5:00 AM | 15 | 1816.9291 |  | 1816.9291 |  | 61.6857 | 2.0847 | 3.8 | 7.5515 | 15.7429 | 4.1429 | OK
| 7/15/2017 6:00 AM | 15 | 1851.9444 |  | 1851.9444 |  | 62.7457 | 2.0778 | 3.6 | 7.4087 | 15.3937 | 4.276 | OK
| 7/15/2017 7:00 AM | 15 | 1858.1548 |  | 1858.1548 |  | 62.9224 | 2.1122 | 3.6 | 7.3839 | 15.5967 | 4.3324 | OK
| 7/15/2017 8:00 AM | 15 | 1850.5521 |  | 1850.5521 |  | 62.8376 | 2.1536 | 3.6 | 7.4143 | 15.9671 | 4.4353 | OK
| 7/15/2017 9:00 AM | 15 | 1867.6101 |  | 1867.6101 |  | 62.5832 | 2.1192 | 3.8 | 7.3466 | 15.5689 | 4.0971 | OK
| 7/15/2017 10:00 AM | 15 | 1833.5265 |  | 1833.5265 |  | 62.403 | 2.0987 | 3.8 | 7.4831 | 15.7045 | 4.1328 | OK
| 7/15/2017 11:00 AM | 15 | 1880.7487 |  | 1880.7487 |  | 61.9861 | 2.0849 | 3.8 | 7.2952 | 15.2095 | 4.0025 | OK
| 7/15/2017 12:00 PM | 15 | 1437.2227 |  | 1437.2227 |  | 61.8235 | 2.0987 | 3.8 | 9.5465 | 20.0349 | 5.2724 | OK
| 7/15/2017 1:00 PM | 15 | 1453.424 |  | 1453.424 |  | 62.5266 | 2.0987 | 3.8 | 9.4401 | 19.8116 | 5.2136 | OK
| 7/15/2017 2:00 PM | 15 | 1450.0725 |  | 1450.0725 |  | 63.2757 | 2.1124 | 3.6 | 9.462 | 19.987 | 5.5519 | OK
| 7/15/2017 3:00 PM | 15 | 1427.7249 |  | 1427.7249 |  | 63.6926 | 2.1263 | 3.6 | 9.6101 | 20.4335 | 5.676 | OK
| 7/15/2017 4:00 PM | 15 | 1452.6744 |  | 1452.6744 |  | 63.7774 | 2.1193 | 3.6 | 9.445 | 20.0169 | 5.5603 | OK
| 7/15/2017 5:00 PM | 15 | 1442.3947 |  | 1442.3947 |  | 63.841 | 2.1193 | 3.6 | 9.5123 | 20.1596 | 5.5999 | OK
| 7/15/2017 6:00 PM | 15 | 1444.7507 |  | 1444.7507 |  | 62.516 | 2.1125 | 3.8 | 9.4968 | 20.0616 | 5.2794 | OK
| 7/15/2017 7:00 PM | 15 | 1447.4277 |  | 1447.4277 |  | 61.6398 | 2.1056 | 3.8 | 9.4792 | 19.9596 | 5.2525 | OK
| 7/15/2017 8:00 PM | 15 | 1863.1127 |  | 1863.1127 |  | 60.0922 | 2.0849 | 4 | 7.3643 | 15.3535 | 3.8384 | OK
| 7/15/2017 9:00 PM | 15 | 1873.2852 |  | 1873.2852 |  | 60.0852 | 2.0779 | 4 | 7.3243 | 15.2192 | 3.8048 | OK
| 7/15/2017 10:00 PM | 15 | 1869.9339 |  | 1869.9339 |  | 62.0391 | 2.0504 | 3.8 | 7.3374 | 15.0446 | 3.9591 | OK
| 7/15/2017 11:00 PM | 15 | 1848.7641 |  | 1848.7641 |  | 64.0212 | 2.0779 | 3.6 | 7.4215 | 15.421 | 4.2836 | OK
| 7/16/2017 12:00 AM | 16 | 1817.0683 |  | 1817.0683 |  | 65.0352 | 2.0779 | 3.4 | 7.5509 | 15.69 | 4.6147 | OK
| 7/16/2017 1:00 AM | 16 | 1853.9038 |  | 1853.9038 |  | 66.5687 | 2.0847 | 3.2 | 7.4009 | 15.429 | 4.8215 | OK
| 7/16/2017 2:00 AM | 16 | 1842.9819 |  | 1842.9819 |  | 68.1198 | 2.0917 | 3 | 7.4447 | 15.5722 | 5.1907 | OK
| 7/16/2017 3:00 AM | 16 | 1863.2948 |  | 1863.2948 |  | 68.1445 | 2.0917 | 3 | 7.3636 | 15.4024 | 5.1341 | OK
| 7/16/2017 4:00 AM | 16 | 1841.6965 |  | 1841.6965 |  | 67.6569 | 2.0986 | 3.2 | 7.4499 | 15.6341 | 4.8856 | OK
| 7/16/2017 5:00 AM | 16 | 1879.7103 |  | 1879.7103 |  | 67.6852 | 2.0987 | 3.2 | 7.2993 | 15.3187 | 4.7871 | OK
| 7/16/2017 6:00 AM | 16 | 1831.3848 |  | 1831.3848 |  | 67.1764 | 2.078 | 3.2 | 7.4919 | 15.5682 | 4.865 | OK
| 7/16/2017 7:00 AM | 16 | 1858.2619 |  | 1858.2619 |  | 66.4238 | 2.1056 | 3.2 | 7.3835 | 15.5468 | 4.8584 | OK
| 7/16/2017 8:00 AM | 16 | 1871.1439 |  | 1871.1439 |  | 66.0034 | 2.1124 | 3.4 | 7.3327 | 15.4892 | 4.5557 | OK
| 7/16/2017 9:00 AM | 16 | 1873.1783 |  | 1873.1783 |  | 65.5688 | 2.0643 | 3.4 | 7.3247 | 15.1205 | 4.4472 | OK
| 7/16/2017 10:00 AM | 16 | 1866.2181 |  | 1866.2181 |  | 64.7173 | 2.0988 | 3.4 | 7.352 | 15.4302 | 4.5383 | OK
| 7/16/2017 11:00 AM | 16 | 1863.1127 |  | 1863.1127 |  | 64.53 | 2.0677 | 3.4 | 7.3643 | 15.2274 | 4.4786 | OK
| 7/16/2017 12:00 PM | 16 | 1869.4303 |  | 1869.4303 |  | 63.7845 | 2.0713 | 3.6 | 7.3394 | 15.2018 | 4.2227 | OK
| 7/16/2017 1:00 PM | 16 | 1871.465 |  | 1871.465 |  | 63.2545 | 2.0712 | 3.6 | 7.3314 | 15.1845 | 4.2179 | OK
| 7/16/2017 2:00 PM | 16 | 1849.3743 |  | 1849.3743 |  | 62.562 | 2.085 | 3.8 | 7.419 | 15.4683 | 4.0706 | OK
| 7/16/2017 3:00 PM | 16 | 1865.4686 |  | 1865.4686 |  | 61.8553 | 2.0781 | 3.8 | 7.355 | 15.2845 | 4.0222 | OK
| 7/16/2017 4:00 PM | 16 | 1871.1439 |  | 1871.1439 |  | 61.2865 | 2.0918 | 3.8 | 7.3327 | 15.3386 | 4.0365 | OK
| 7/16/2017 5:00 PM | 16 | 1858.8295 |  | 1858.8295 |  | 64.265 | 2.0643 | 3.6 | 7.3813 | 15.2372 | 4.2326 | OK
| 7/16/2017 6:00 PM | 16 | 1865.4686 |  | 1865.4686 |  | 62.0709 | 2.0643 | 3.8 | 7.355 | 15.183 | 3.9955 | OK
| 7/16/2017 7:00 PM | 16 | 1860.7569 |  | 1860.7569 |  | 60.6505 | 2.0369 | 4 | 7.3736 | 15.0194 | 3.7549 | OK
| 7/16/2017 8:00 PM | 16 | 1860.65 |  | 1860.65 |  | 60.9119 | 2.0439 | 3.8 | 7.374 | 15.0716 | 3.9662 | OK
| 7/16/2017 9:00 PM | 16 | 1872.9642 |  | 1872.9642 |  | 61.8094 | 2.0847 | 3.8 | 7.3256 | 15.2719 | 4.0189 | OK
| 7/16/2017 10:00 PM | 16 | 1870.9294 |  | 1870.9294 |  | 63.3393 | 2.0849 | 3.6 | 7.3335 | 15.2893 | 4.247 | OK
| 7/16/2017 11:00 PM | 16 | 1883.7793 |  | 1883.7793 |  | 64.5583 | 2.071 | 3.4 | 7.2835 | 15.0845 | 4.4366 | OK
| 7/17/2017 12:00 AM | 17 | 1843.7313 |  | 1843.7313 |  | 66.8407 | 2.0847 | 3.2 | 7.4417 | 15.5141 | 4.8481 | OK
| 7/17/2017 1:00 AM | 17 | 1876.4976 |  | 1876.4976 |  | 67.8194 | 2.0779 | 3.2 | 7.3118 | 15.1931 | 4.7478 | OK
| 7/17/2017 2:00 AM | 17 | 1859.3649 |  | 1859.3649 |  | 67.1269 | 2.0505 | 3.2 | 7.3791 | 15.1309 | 4.7284 | OK
| 7/17/2017 3:00 AM | 17 | 1866.9677 |  | 1866.9677 |  | 68.0597 | 2.071 | 3 | 7.3491 | 15.2203 | 5.0734 | OK
| 7/17/2017 4:00 AM | 17 | 2075.5598 |  | 2075.5598 |  | 68.2152 | 2.0574 | 3 | 6.6105 | 13.6001 | 4.5334 | OK
| 7/17/2017 5:00 AM | 17 | 2062.9992 |  | 2062.9992 |  | 67.5863 | 2.0642 | 3.2 | 6.6508 | 13.7285 | 4.2902 | OK
| 7/17/2017 6:00 AM | 17 | 2046.6483 |  | 2046.6483 |  | 66.9008 | 2.0987 | 3.2 | 6.7039 | 14.0692 | 4.3966 | OK
| 7/17/2017 7:00 AM | 17 | 2044.9026 |  | 2044.9026 |  | 66.3567 | 2.1125 | 3.2 | 6.7096 | 14.1738 | 4.4293 | OK
| 7/17/2017 8:00 AM | 17 | 2082.2736 |  | 2082.2736 |  | 66.0528 | 2.1192 | 3.4 | 6.5892 | 13.9639 | 4.107 | OK
| 7/17/2017 9:00 AM | 17 | 2075.2385 |  | 2075.2385 |  | 66.8301 | 2.0918 | 3.2 | 6.6115 | 13.8301 | 4.3219 | OK
| 7/17/2017 10:00 AM | 17 | 2063.6417 |  | 2063.6417 |  | 65.3144 | 2.071 | 3.4 | 6.6487 | 13.7698 | 4.0499 | OK
| 7/17/2017 11:00 AM | 17 | 2051.6488 |  | 2051.6488 |  | 64.5229 | 2.0644 | 3.4 | 6.6876 | 13.8059 | 4.0606 | OK
| 7/17/2017 12:00 PM | 17 | 2062.8171 |  | 2062.8171 |  | 63.7315 | 2.085 | 3.6 | 6.6513 | 13.8678 | 3.8522 | OK
| 7/17/2017 1:00 PM | 17 | 2053.6086 |  | 2053.6086 |  | 63.2863 | 2.0507 | 3.6 | 6.6812 | 13.7012 | 3.8059 | OK
| 7/17/2017 2:00 PM | 17 | 2047.6118 |  | 2047.6118 |  | 63.7915 | 2.0506 | 3.6 | 6.7007 | 13.7406 | 3.8168 | OK
| 7/17/2017 3:00 PM | 17 | 2081.0207 |  | 2081.0207 |  | 64.265 | 2.0712 | 3.6 | 6.5932 | 13.6555 | 3.7932 | OK
| 7/17/2017 4:00 PM | 17 | 2063.781 |  | 2063.781 |  | 62.3465 | 2.0644 | 3.8 | 6.6482 | 13.7247 | 3.6118 | OK
| 7/17/2017 5:00 PM | 17 | 2065.0659 |  | 2065.0659 |  | 61.9719 | 2.037 | 3.8 | 6.6441 | 13.5342 | 3.5616 | OK
| 7/17/2017 6:00 PM | 17 | 2043.0074 |  | 2043.0074 |  | 65.2861 | 2.0026 | 3.4 | 6.7158 | 13.4489 | 3.9556 | OK
| 7/17/2017 7:00 PM | 17 | 2058.6411 |  | 2058.6411 |  | 66.392 | 2.0163 | 3.2 | 6.6648 | 13.438 | 4.1994 | OK
| 7/17/2017 8:00 PM | 17 | 2043.0823 |  | 2043.0823 |  | 66.8372 | 2.0301 | 3.2 | 6.7156 | 13.6331 | 4.2603 | OK
| 7/17/2017 9:00 PM | 17 | 2066.0297 |  | 2066.0297 |  | 68.2682 | 2.0643 | 3 | 6.641 | 13.7091 | 4.5697 | OK
| 7/17/2017 10:00 PM | 17 | 2039.6881 |  | 2039.6881 |  | 68.6074 | 2.0232 | 3 | 6.7268 | 13.6097 | 4.5366 | OK
| 7/17/2017 11:00 PM | 17 | 2065.4621 |  | 2065.4621 |  | 69.049 | 2.0574 | 3 | 6.6428 | 13.6666 | 4.5555 | OK
| 7/18/2017 12:00 AM | 18 | 2047.6867 |  | 2047.6867 |  | 69.3105 | 2.0162 | 3 | 6.7005 | 13.5092 | 4.5031 | OK
| 7/18/2017 1:00 AM | 18 | 2037.8675 |  | 2037.8675 |  | 69.155 | 2.03 | 3 | 6.7328 | 13.6672 | 4.5557 | OK
| 7/18/2017 2:00 AM | 18 | 2063.5668 |  | 2063.5668 |  | 69.6603 | 2.0506 | 3 | 6.6489 | 13.6344 | 4.5448 | OK
| 7/18/2017 3:00 AM | 18 | 2034.8372 |  | 2034.8372 |  | 68.724 | 2.0025 | 3 | 6.7428 | 13.5022 | 4.5007 | OK
| 7/18/2017 4:00 AM | 18 | 2061.393 |  | 2061.393 |  | 63.6078 | 2.0643 | 3.6 | 6.6559 | 13.7399 | 3.8166 | OK
| 7/18/2017 5:00 AM | 18 | 2027.3417 |  | 2027.3417 |  | 63.7315 | 2.0368 | 3.6 | 6.7677 | 13.7846 | 3.829 | OK
| 7/18/2017 6:00 AM | 18 | 2057.3239 |  | 2057.3239 |  | 65.2861 | 2.037 | 3.4 | 6.6691 | 13.5851 | 3.9956 | OK
| 7/18/2017 7:00 AM | 18 | 2035.8009 |  | 2035.8009 |  | 65.2084 | 2.1055 | 3.4 | 6.7396 | 14.1903 | 4.1736 | OK
| 7/18/2017 8:00 AM | 18 | 925.3797 |  | 925.3797 |  | 65.0635 | 2.1399 | 3.4 | 14.8269 | 31.7275 | 9.3316 | OK
| 7/18/2017 9:00 AM | 18 | 927.8425 |  | 927.8425 |  | 64.7597 | 2.1056 | 3.4 | 14.7875 | 31.1369 | 9.1579 | OK
| 7/18/2017 10:00 AM | 18 | 955.7904 |  | 955.7904 |  | 64.5194 | 2.1056 | 3.4 | 14.3552 | 30.2264 | 8.8901 | OK
| 7/18/2017 11:00 AM | 18 | 972.3878 |  | 972.3878 |  | 64.3639 | 2.0918 | 3.6 | 14.1101 | 29.5157 | 8.1988 | OK
| 7/18/2017 12:00 PM | 18 | 927.3072 |  | 927.3072 |  | 64.2226 | 2.0781 | 3.6 | 14.7961 | 30.7479 | 8.5411 | OK
| 7/18/2017 1:00 PM | 18 | 941.4417 |  | 941.4417 |  | 64.1166 | 2.1539 | 3.6 | 14.5739 | 31.3905 | 8.7196 | OK
| 7/18/2017 2:00 PM | 18 | 938.5506 |  | 938.5506 |  | 64.583 | 2.1676 | 3.4 | 14.6188 | 31.6874 | 9.3198 | OK
| 7/18/2017 3:00 PM | 18 | 954.5056 |  | 954.5056 |  | 64.8657 | 2.0851 | 3.4 | 14.3745 | 29.9717 | 8.8152 | OK
| 7/18/2017 4:00 PM | 18 | 937.2978 |  | 937.2978 |  | 65.3002 | 2.1126 | 3.4 | 14.6384 | 30.9246 | 9.0955 | OK
| 7/18/2017 5:00 PM | 18 | 938.6898 |  | 938.6898 |  | 65.3638 | 2.1744 | 3.4 | 14.6167 | 31.7828 | 9.3479 | OK
| 7/18/2017 6:00 PM | 18 | 938.3687 |  | 938.3687 |  | 64.7243 | 2.1813 | 3.4 | 14.6217 | 31.8938 | 9.3805 | OK
| 7/18/2017 7:00 PM | 18 | 951.8607 |  | 951.8607 |  | 63.8834 | 2.1813 | 3.6 | 14.4144 | 31.4418 | 8.7338 | OK
| 7/18/2017 8:00 PM | 18 | 946.935 |  | 946.935 |  | 63.6325 | 2.1881 | 3.6 | 14.4894 | 31.7045 | 8.8068 | OK
| 7/18/2017 9:00 PM | 18 | 947.3634 |  | 947.3634 |  | 63.3888 | 2.1881 | 3.6 | 14.4828 | 31.6902 | 8.8028 | OK
| 7/18/2017 10:00 PM | 18 | 1738.3645 |  | 1738.3645 |  | 62.1875 | 2.14 | 3.8 | 7.8928 | 16.8903 | 4.4448 | OK
| 7/18/2017 11:00 PM | 18 | 1744.254 |  | 1744.254 |  | 61.8235 | 2.14 | 3.8 | 7.8661 | 16.8332 | 4.4298 | OK
| 7/19/2017 12:00 AM | 19 | 1759.1056 |  | 1759.1056 |  | 61.2511 | 1.9336 | 3.8 | 7.7997 | 15.0819 | 3.9689 | OK
| 7/19/2017 1:00 AM | 19 | 1748.5049 |  | 1748.5049 |  | 62.2263 | 2.03 | 3.8 | 7.847 | 15.9291 | 4.1919 | OK
| 7/19/2017 2:00 AM | 19 | 1763.3139 |  | 1763.3139 |  | 64.1025 | 2.03 | 3.6 | 7.7811 | 15.7953 | 4.3876 | OK
| 7/19/2017 3:00 AM | 19 | 1737.8291 |  | 1737.8291 |  | 64.3569 | 2.0093 | 3.6 | 7.8952 | 15.8638 | 4.4066 | OK
| 7/19/2017 4:00 AM | 19 | 1757.2854 |  | 1757.2854 |  | 64.3604 | 2.0093 | 3.6 | 7.8078 | 15.6882 | 4.3578 | OK
| 7/19/2017 5:00 AM | 19 | 1747.434 |  | 1747.434 |  | 64.8021 | 2.0231 | 3.4 | 7.8518 | 15.885 | 4.6721 | OK
| 7/19/2017 6:00 AM | 19 | 2046.0806 |  | 2046.0806 |  | 65.9892 | 2.0231 | 3.4 | 6.7058 | 13.5665 | 3.9901 | OK
| 7/19/2017 7:00 AM | 19 | 2027.3417 |  | 2027.3417 |  | 66.6535 | 2.0094 | 3.2 | 6.7677 | 13.5992 | 4.2497 | OK
| 7/19/2017 8:00 AM | 19 | 1259.1486 |  | 1259.1486 |  | 66.6146 | 1.9613 | 3.2 | 10.8967 | 21.3711 | 6.6785 | OK
| 7/19/2017 9:00 AM | 19 | 1608.7972 |  | 1608.7972 |  | 66.5121 | 1.9881 | 3.2 | 8.5284 | 16.9555 | 5.2986 | OK
| 7/19/2017 10:00 AM | 19 | 2028.8407 |  | 2028.8407 |  | 66.1235 | 2.0018 | 3.4 | 6.7627 | 13.5377 | 3.9817 | OK
| 7/19/2017 11:00 AM | 19 | 2051.7878 |  | 2051.7878 |  | 65.9928 | 1.9745 | 3.4 | 6.6871 | 13.2038 | 3.8835 | OK
| 7/19/2017 12:00 PM | 19 | 2055.2897 |  | 2055.2897 |  | 65.5334 | 1.9538 | 3.4 | 6.6757 | 13.0427 | 3.8361 | OK
| 7/19/2017 1:00 PM | 19 | 2095.798 |  | 2095.798 |  | 65.0458 | 1.9402 | 3.4 | 6.5467 | 12.7017 | 3.7358 | OK
| 7/19/2017 2:00 PM | 19 | 509.2984 |  | 509.2984 |  | 65.5228 | 2.0639 | 3.4 | 26.94 | 55.601 | 16.3532 | OK
| 7/19/2017 3:00 PM | 19 | 2042.5792 |  | 2042.5792 |  | 64.7702 | 2.0366 | 3.4 | 6.7173 | 13.6803 | 4.0236 | OK
| 7/19/2017 4:00 PM | 19 | 2049.8926 |  | 2049.8926 |  | 64.5547 | 2.0228 | 3.4 | 6.6933 | 13.5391 | 3.9821 | OK
| 7/19/2017 5:00 PM | 19 | 984.595 |  | 984.595 |  | 65.1872 | 1.9677 | 3.4 | 13.9352 | 27.4199 | 8.0647 | OK
| 7/19/2017 6:00 PM | 19 | 914.5969 |  | 914.5969 |  | 64.3675 | 2.0775 | 3.6 | 15.0017 | 31.1656 | 8.6571 | OK
| 7/19/2017 7:00 PM | 19 | 931.3761 |  | 931.3761 |  | 64.3321 | 2.0432 | 3.6 | 14.7314 | 30.0997 | 8.361 | OK
| 7/19/2017 8:00 PM | 19 | 929.4488 |  | 929.4488 |  | 63.9611 | 2.0295 | 3.6 | 14.762 | 29.9599 | 8.3222 | OK
| 7/19/2017 9:00 PM | 19 | 1410.0244 |  | 1410.0244 |  | 63.5018 | 2.0157 | 3.6 | 9.7307 | 19.6144 | 5.4484 | OK
| 7/19/2017 10:00 PM | 19 | 1439.9 |  | 1439.9 |  | 63.8551 | 1.9539 | 3.6 | 9.5288 | 18.618 | 5.1717 | OK
| 7/19/2017 11:00 PM | 19 | 1426.622 |  | 1426.622 |  | 63.0425 | 1.9539 | 3.6 | 9.6175 | 18.7913 | 5.2198 | OK
| 7/20/2017 12:00 AM | 20 | 1438.9362 |  | 1438.9362 |  | 64.0848 | 1.9125 | 3.6 | 9.5352 | 18.2356 | 5.0654 | OK
| 7/20/2017 1:00 AM | 20 | 1430.6911 |  | 1430.6911 |  | 64.1413 | 1.9331 | 3.6 | 9.5901 | 18.5388 | 5.1497 | OK
| 7/20/2017 2:00 AM | 20 | 1428.7637 |  | 1428.7637 |  | 64.3392 | 1.9331 | 3.6 | 9.6031 | 18.5638 | 5.1566 | OK
| 7/20/2017 3:00 AM | 20 | 942.2984 |  | 942.2984 |  | 64.5795 | 1.9331 | 3.4 | 14.5607 | 28.1474 | 8.2786 | OK
| 7/20/2017 4:00 AM | 20 | 929.5559 |  | 929.5559 |  | 64.8233 | 1.9263 | 3.4 | 14.7603 | 28.4322 | 8.3624 | OK
| 7/20/2017 5:00 AM | 20 | 920.347 |  | 920.347 |  | 64.7915 | 1.9538 | 3.4 | 14.908 | 29.1266 | 8.5667 | OK
| 7/20/2017 6:00 AM | 20 | 950.9719 |  | 950.9719 |  | 64.9893 | 1.9881 | 3.4 | 14.4279 | 28.6843 | 8.4365 | OK
| 7/20/2017 7:00 AM | 20 | 929.77 |  | 929.77 |  | 65.2437 | 1.9814 | 3.4 | 14.7569 | 29.2389 | 8.5997 | OK
| 7/20/2017 8:00 AM | 20 | 943.7974 |  | 943.7974 |  | 65.2967 | 2.0019 | 3.4 | 14.5376 | 29.103 | 8.5597 | OK
| 7/20/2017 9:00 AM | 20 | 928.2708 |  | 928.2708 |  | 64.848 | 2.0018 | 3.4 | 14.7807 | 29.5882 | 8.7024 | OK
| 7/20/2017 10:00 AM | 20 | 967.6765 |  | 967.6765 |  | 63.6679 | 1.9951 | 3.6 | 14.1788 | 28.2877 | 7.8577 | OK
| 7/20/2017 11:00 AM | 20 | 965.3527 |  | 965.3527 |  | 63.2686 | 2.0157 | 3.6 | 14.213 | 28.6494 | 7.9582 | OK
| 7/20/2017 12:00 PM | 20 | 974.5617 |  | 974.5617 |  | 63.0496 | 2.0157 | 3.6 | 14.0787 | 28.3787 | 7.883 | OK
| 7/20/2017 1:00 PM | 20 | 956.4652 |  | 956.4652 |  | 63.4877 | 2.1393 | 3.6 | 14.345 | 30.6886 | 8.5246 | OK
| 7/20/2017 2:00 PM | 20 | 952.364 |  | 952.364 |  | 63.4276 | 2.1668 | 3.6 | 14.4068 | 31.217 | 8.6714 | OK
| 7/20/2017 3:00 PM | 20 | 958.1785 |  | 958.1785 |  | 63.2863 | 2.1875 | 3.6 | 14.3194 | 31.3233 | 8.7009 | OK
| 7/20/2017 4:00 PM | 20 | 955.5014 |  | 955.5014 |  | 63.1591 | 2.2015 | 3.6 | 14.3595 | 31.6124 | 8.7812 | OK
| 7/20/2017 5:00 PM | 20 | 1352.5546 |  | 1352.5546 |  | 62.9824 | 2.1878 | 3.6 | 10.1441 | 22.1934 | 6.1648 | OK
| 7/20/2017 6:00 PM | 20 | 1360.0823 |  | 1360.0823 |  | 62.7563 | 2.1464 | 3.6 | 10.088 | 21.6527 | 6.0147 | OK
| 7/20/2017 7:00 PM | 20 | 1342.414 |  | 1342.414 |  | 62.4807 | 2.1739 | 3.8 | 10.2208 | 22.2188 | 5.8471 | OK
| 7/20/2017 8:00 PM | 20 | 1350.5201 |  | 1350.5201 |  | 62.1804 | 2.1666 | 3.8 | 10.1594 | 22.0115 | 5.7925 | OK
| 7/20/2017 9:00 PM | 20 | 1445.4252 |  | 1445.4252 |  | 61.3253 | 2.1326 | 3.8 | 9.4924 | 20.2433 | 5.3272 | OK
| 7/20/2017 10:00 PM | 20 | 1443.2515 |  | 1443.2515 |  | 60.9897 | 2.1188 | 3.8 | 9.5067 | 20.1425 | 5.3007 | OK
| 7/20/2017 11:00 PM | 20 | 1454.1738 |  | 1454.1738 |  | 60.6328 | 2.1531 | 4 | 9.4353 | 20.3153 | 5.0788 | OK
| 7/21/2017 12:00 AM | 21 | 1597.1256 |  | 1597.1256 |  | 62.5478 | 2.1463 | 3.8 | 8.5908 | 18.4382 | 4.8521 | OK
| 7/21/2017 1:00 AM | 21 | 1846.1942 |  | 1846.1942 |  | 63.4488 | 2.1393 | 3.6 | 7.4318 | 15.899 | 4.4164 | OK
| 7/21/2017 2:00 AM | 21 | 1849.0853 |  | 1849.0853 |  | 63.1167 | 2.1393 | 3.6 | 7.4202 | 15.8741 | 4.4095 | OK
| 7/21/2017 3:00 AM | 21 | 1831.8455 |  | 1831.8455 |  | 64.5088 | 2.1393 | 3.4 | 7.49 | 16.0235 | 4.7128 | OK
| 7/21/2017 4:00 AM | 21 | 1430.22 |  | 1430.22 |  | 65.166 | 2.2903 | 3.4 | 9.5933 | 21.9717 | 6.4623 | OK
| 7/21/2017 5:00 AM | 21 | 1647.3461 |  | 1647.3461 |  | 65.2437 | 2.2707 | 3.4 | 8.3289 | 18.9126 | 5.5625 | OK
| 7/21/2017 6:00 AM | 21 | 1647.9888 |  | 1647.9888 |  | 65.3462 | 2.2834 | 3.4 | 8.3256 | 19.0104 | 5.5913 | OK
| 7/21/2017 7:00 AM | 21 | 1647.132 |  | 1647.132 |  | 63.9435 | 2.3176 | 3.6 | 8.3299 | 19.3055 | 5.3626 | OK
| 7/21/2017 8:00 AM | 21 | 933.0146 |  | 933.0146 |  | 63.5054 | 2.3589 | 3.6 | 14.7056 | 34.6892 | 9.6359 | OK
| 7/21/2017 9:00 AM | 21 | 925.4119 |  | 925.4119 |  | 63.9187 | 2.3938 | 3.6 | 14.8264 | 35.4914 | 9.8587 | OK
| 7/21/2017 10:00 AM | 21 | 936.0128 |  | 936.0128 |  | 64.9186 | 2.3802 | 3.4 | 14.6585 | 34.8902 | 10.2618 | OK
| 7/21/2017 11:00 AM | 21 | 957.1076 |  | 957.1076 |  | 65.2084 | 2.3734 | 3.4 | 14.3354 | 34.0231 | 10.0068 | OK
| 7/21/2017 12:00 PM | 21 | 939.3324 |  | 939.3324 |  | 65.6818 | 2.3321 | 3.4 | 14.6067 | 34.0635 | 10.0187 | OK
| 7/21/2017 1:00 PM | 21 | 933.7642 |  | 933.7642 |  | 65.703 | 2.3253 | 3.4 | 14.6938 | 34.1676 | 10.0493 | OK
| 7/21/2017 2:00 PM | 21 | 940.1889 |  | 940.1889 |  | 65.6324 | 2.3185 | 3.4 | 14.5934 | 33.8342 | 9.9512 | OK
| 7/21/2017 3:00 PM | 21 | 934.7278 |  | 934.7278 |  | 65.5264 | 2.3322 | 3.4 | 14.6786 | 34.2329 | 10.0685 | OK
| 7/21/2017 4:00 PM | 21 | 930.4447 |  | 930.4447 |  | 65.4027 | 2.339 | 3.4 | 14.7462 | 34.4915 | 10.1446 | OK
| 7/21/2017 5:00 PM | 21 | 947.8987 |  | 947.8987 |  | 65.1518 | 2.339 | 3.4 | 14.4747 | 33.8564 | 9.9578 | OK
| 7/21/2017 6:00 PM | 21 | 941.0778 |  | 941.0778 |  | 64.6678 | 2.3459 | 3.4 | 14.5796 | 34.2016 | 10.0593 | OK
| 7/21/2017 7:00 PM | 21 | 1533.7665 |  | 1533.7665 |  | 64.2897 | 2.3665 | 3.6 | 8.9456 | 21.17 | 5.8805 | OK
| 7/21/2017 8:00 PM | 21 | 1536.9466 |  | 1536.9466 |  | 63.9187 | 2.2222 | 3.6 | 8.9271 | 19.8374 | 5.5104 | OK
| 7/21/2017 9:00 PM | 21 | 1799.4 |  | 1799.4 |  | 63.6149 | 2.2153 | 3.6 | 7.6251 | 16.8918 | 4.6922 | OK
| 7/21/2017 10:00 PM | 21 | 1784.5482 |  | 1784.5482 |  | 63.1591 | 2.2153 | 3.6 | 7.6885 | 17.0324 | 4.7312 | OK
| 7/21/2017 11:00 PM | 21 | 1796.6481 |  | 1796.6481 |  | 63.3287 | 2.2152 | 3.6 | 7.6367 | 16.9168 | 4.6991 | OK
| 7/22/2017 12:00 AM | 22 | 1772.127 |  | 1772.127 |  | 64.9928 | 2.2153 | 3.4 | 7.7424 | 17.1518 | 5.0446 | OK
| 7/22/2017 1:00 AM | 22 | 1807.7844 |  | 1807.7844 |  | 65.1059 | 2.2083 | 3.4 | 7.5897 | 16.7607 | 4.9296 | OK
| 7/22/2017 2:00 AM | 22 | 1788.6922 |  | 1788.6922 |  | 65.8408 | 2.1741 | 3.4 | 7.6707 | 16.6769 | 4.905 | OK
| 7/22/2017 3:00 AM | 22 | 1803.0408 |  | 1803.0408 |  | 67.2718 | 2.1945 | 3.2 | 7.6097 | 16.6997 | 5.2187 | OK
| 7/22/2017 4:00 AM | 22 | 1829.0615 |  | 1829.0615 |  | 65.8373 | 2.1945 | 3.4 | 7.5014 | 16.4621 | 4.8418 | OK
| 7/22/2017 5:00 AM | 22 | 1834.201 |  | 1834.201 |  | 67.1976 | 2.2015 | 3.2 | 7.4804 | 16.468 | 5.1463 | OK
| 7/22/2017 6:00 AM | 22 | 1850.2631 |  | 1850.2631 |  | 67.5757 | 2.1945 | 3.2 | 7.4154 | 16.2735 | 5.0855 | OK
| 7/22/2017 7:00 AM | 22 | 1482.4428 |  | 1482.4428 |  | 67.77 | 2.2289 | 3.2 | 9.2553 | 20.6292 | 6.4466 | OK
| 7/22/2017 8:00 AM | 22 | 1200.9292 |  | 1200.9292 |  | 67.7029 | 2.2358 | 3.2 | 11.4249 | 25.5444 | 7.9826 | OK
| 7/22/2017 9:00 AM | 22 | 1183.8285 |  | 1183.8285 |  | 67.3389 | 2.2565 | 3.2 | 11.59 | 26.1528 | 8.1727 | OK
| 7/22/2017 10:00 AM | 22 | 1432.9716 |  | 1432.9716 |  | 66.9255 | 2.1878 | 3.2 | 9.5749 | 20.9479 | 6.5462 | OK
| 7/22/2017 11:00 AM | 22 | 1447.2136 |  | 1447.2136 |  | 66.6005 | 2.1603 | 3.2 | 9.4806 | 20.481 | 6.4003 | OK
| 7/22/2017 12:00 PM | 22 | 1650.3444 |  | 1650.3444 |  | 66.2153 | 2.1673 | 3.2 | 8.3137 | 18.018 | 5.6306 | OK
| 7/22/2017 1:00 PM | 22 | 1652.9464 |  | 1652.9464 |  | 65.6253 | 2.181 | 3.4 | 8.3006 | 18.1033 | 5.3245 | OK
| 7/22/2017 2:00 PM | 22 | 1646.811 |  | 1646.811 |  | 65.2896 | 2.1467 | 3.4 | 8.3316 | 17.8854 | 5.2604 | OK
| 7/22/2017 3:00 PM | 22 | 1651.9505 |  | 1651.9505 |  | 64.3145 | 2.181 | 3.6 | 8.3056 | 18.1142 | 5.0317 | OK
| 7/22/2017 4:00 PM | 22 | 1663.8366 |  | 1663.8366 |  | 64.1131 | 2.1879 | 3.6 | 8.2463 | 18.0422 | 5.0117 | OK
| 7/22/2017 5:00 PM | 22 | 1669.8331 |  | 1669.8331 |  | 63.152 | 2.174 | 3.6 | 8.2167 | 17.8631 | 4.962 | OK
| 7/22/2017 6:00 PM | 22 | 1346.1297 |  | 1346.1297 |  | 63.41 | 2.1946 | 3.6 | 10.1926 | 22.3691 | 6.2136 | OK
| 7/22/2017 7:00 PM | 22 | 1725.4077 |  | 1725.4077 |  | 62.2617 | 2.1878 | 3.8 | 7.952 | 17.3975 | 4.5783 | OK
| 7/22/2017 8:00 PM | 22 | 1756.5679 |  | 1756.5679 |  | 61.9119 | 2.1808 | 3.8 | 7.811 | 17.0345 | 4.4828 | OK
| 7/22/2017 9:00 PM | 22 | 1753.3555 |  | 1753.3555 |  | 61.8306 | 2.1877 | 3.8 | 7.8253 | 17.1193 | 4.5051 | OK
| 7/22/2017 10:00 PM | 22 | 1747.9266 |  | 1747.9266 |  | 61.9719 | 2.1945 | 3.8 | 7.8496 | 17.2263 | 4.5332 | OK
| 7/22/2017 11:00 PM | 22 | 1757.2426 |  | 1757.2426 |  | 62.9118 | 2.1945 | 3.6 | 7.808 | 17.1349 | 4.7597 | OK
| 7/23/2017 12:00 AM | 23 | 1947.7384 |  | 1947.7384 |  | 65.9115 | 2.1944 | 3.4 | 7.0443 | 15.4583 | 4.5466 | OK
| 7/23/2017 1:00 AM | 23 | 1947.9202 |  | 1947.9202 |  | 66.5581 | 2.1877 | 3.2 | 7.0437 | 15.4094 | 4.8154 | OK
| 7/23/2017 2:00 AM | 23 | 1955.2017 |  | 1955.2017 |  | 67.8406 | 2.1807 | 3.2 | 7.0174 | 15.3032 | 4.7822 | OK
| 7/23/2017 3:00 AM | 23 | 1948.5627 |  | 1948.5627 |  | 67.9784 | 2.1877 | 3.2 | 7.0414 | 15.4043 | 4.8138 | OK
| 7/23/2017 4:00 AM | 23 | 1961.4871 |  | 1961.4871 |  | 67.7558 | 2.1877 | 3.2 | 6.995 | 15.3028 | 4.7821 | OK
| 7/23/2017 5:00 AM | 23 | 1950.0617 |  | 1950.0617 |  | 67.717 | 2.1877 | 3.2 | 7.0359 | 15.3925 | 4.8101 | OK
| 7/23/2017 6:00 AM | 23 | 993.4079 |  | 993.4079 |  | 67.7134 | 2.1878 | 3.2 | 13.8116 | 30.2169 | 9.4428 | OK
| 7/23/2017 7:00 AM | 23 | 1228.5559 |  | 1228.5559 |  | 67.2506 | 2.2289 | 3.2 | 11.168 | 24.8923 | 7.7788 | OK
| 7/23/2017 8:00 AM | 23 | 946.935 |  | 946.935 |  | 66.9785 | 2.2495 | 3.2 | 14.4894 | 32.5946 | 10.1858 | OK
| 7/23/2017 9:00 AM | 23 | 945.543 |  | 945.543 |  | 66.8372 | 2.2769 | 3.2 | 14.5107 | 33.0401 | 10.325 | OK
| 7/23/2017 10:00 AM | 23 | 938.0473 |  | 938.0473 |  | 66.7524 | 2.2976 | 3.2 | 14.6267 | 33.6062 | 10.5019 | OK
| 7/23/2017 11:00 AM | 23 | 951.2182 |  | 951.2182 |  | 66.2825 | 2.2635 | 3.2 | 14.4242 | 32.6485 | 10.2026 | OK
| 7/23/2017 12:00 PM | 23 | 975.172 |  | 975.172 |  | 65.9716 | 2.3044 | 3.4 | 14.0698 | 32.4232 | 9.5362 | OK
| 7/23/2017 1:00 PM | 23 | 944.5793 |  | 944.5793 |  | 65.7949 | 2.3182 | 3.4 | 14.5255 | 33.6738 | 9.9041 | OK
| 7/23/2017 2:00 PM | 23 | 946.3996 |  | 946.3996 |  | 65.1306 | 2.3252 | 3.4 | 14.4976 | 33.7099 | 9.9147 | OK
| 7/23/2017 3:00 PM | 23 | 923.9128 |  | 923.9128 |  | 64.7279 | 2.3184 | 3.4 | 14.8504 | 34.4286 | 10.1261 | OK
| 7/23/2017 4:00 PM | 23 | 938.6149 |  | 938.6149 |  | 64.5653 | 2.3182 | 3.4 | 14.6178 | 33.8878 | 9.967 | OK
| 7/23/2017 5:00 PM | 23 | 917.8092 |  | 917.8092 |  | 64.1696 | 2.3252 | 3.6 | 14.9492 | 34.76 | 9.6555 | OK
| 7/23/2017 6:00 PM | 23 | 1438.5397 |  | 1438.5397 |  | 63.7032 | 2.3319 | 3.6 | 9.5378 | 22.2417 | 6.1782 | OK
| 7/23/2017 7:00 PM | 23 | 1433.1857 |  | 1433.1857 |  | 63.576 | 2.2977 | 3.6 | 9.5734 | 21.9969 | 6.1103 | OK
| 7/23/2017 8:00 PM | 23 | 1669.4047 |  | 1669.4047 |  | 65.0317 | 2.2085 | 3.4 | 8.2188 | 18.1509 | 5.3385 | OK
| 7/23/2017 9:00 PM | 23 | 1665.764 |  | 1665.764 |  | 64.3427 | 2.1945 | 3.6 | 8.2368 | 18.0759 | 5.0211 | OK
| 7/23/2017 10:00 PM | 23 | 1894.3801 |  | 1894.3801 |  | 63.0814 | 2.1945 | 3.6 | 7.2427 | 15.8945 | 4.4151 | OK
| 7/23/2017 11:00 PM | 23 | 1898.9847 |  | 1898.9847 |  | 61.2582 | 2.2015 | 3.8 | 7.2252 | 15.9062 | 4.1858 | OK
| 7/24/2017 12:00 AM | 24 | 1897.8068 |  | 1897.8068 |  | 61.9719 | 2.1739 | 3.8 | 7.2297 | 15.7165 | 4.1359 | OK
| 7/24/2017 1:00 AM | 24 | 1905.5163 |  | 1905.5163 |  | 64.0212 | 2.174 | 3.6 | 7.2004 | 15.6537 | 4.3482 | OK
| 7/24/2017 2:00 AM | 24 | 1896.7359 |  | 1896.7359 |  | 64.1095 | 2.1808 | 3.6 | 7.2338 | 15.7757 | 4.3821 | OK
| 7/24/2017 3:00 AM | 24 | 1897.0571 |  | 1897.0571 |  | 63.9046 | 2.1807 | 3.6 | 7.2325 | 15.7722 | 4.3812 | OK
| 7/24/2017 4:00 AM | 24 | 1901.2332 |  | 1901.2332 |  | 63.8339 | 2.1877 | 3.6 | 7.2166 | 15.7878 | 4.3855 | OK
| 7/24/2017 5:00 AM | 24 | 1043.4141 |  | 1043.4141 |  | 65.9115 | 2.2016 | 3.4 | 13.1496 | 28.9503 | 8.5148 | OK
| 7/24/2017 6:00 AM | 24 | 1053.801 |  | 1053.801 |  | 66.5051 | 2.1808 | 3.2 | 13.02 | 28.3946 | 8.8733 | OK
| 7/24/2017 7:00 AM | 24 | 1249.7576 |  | 1249.7576 |  | 66.5546 | 2.2152 | 3.2 | 10.9785 | 24.3196 | 7.5999 | OK
| 7/24/2017 8:00 AM | 24 | 1743.2901 |  | 1743.2901 |  | 64.6501 | 2.2152 | 3.4 | 7.8705 | 17.4346 | 5.1278 | OK
| 7/24/2017 9:00 AM | 24 | 1753.8912 |  | 1753.8912 |  | 63.8728 | 2.2015 | 3.6 | 7.8229 | 17.2221 | 4.7839 | OK
| 7/24/2017 10:00 AM | 24 | 1750.5715 |  | 1750.5715 |  | 63.0637 | 2.1739 | 3.6 | 7.8377 | 17.0384 | 4.7329 | OK
| 7/24/2017 11:00 AM | 24 | 1699.6015 |  | 1699.6015 |  | 62.9082 | 2.174 | 3.6 | 8.0728 | 17.5502 | 4.8751 | OK
| 7/24/2017 12:00 PM | 24 | 1345.1662 |  | 1345.1662 |  | 62.1345 | 2.1671 | 3.8 | 10.1999 | 22.1046 | 5.817 | OK
| 7/24/2017 1:00 PM | 24 | 1647.132 |  | 1647.132 |  | 61.6433 | 2.1603 | 3.8 | 8.3299 | 17.9952 | 4.7356 | OK
| 7/24/2017 2:00 PM | 24 | 1653.7711 |  | 1653.7711 |  | 61.3854 | 2.174 | 3.8 | 8.2965 | 18.0366 | 4.7465 | OK
| 7/24/2017 3:00 PM | 24 | 1646.7361 |  | 1646.7361 |  | 61.8589 | 2.167 | 3.8 | 8.3319 | 18.0557 | 4.7515 | OK
| 7/24/2017 4:00 PM | 24 | 1219.379 |  | 1219.379 |  | 61.5656 | 2.1808 | 3.8 | 11.2521 | 24.539 | 6.4576 | OK
| 7/24/2017 5:00 PM | 24 | 1204.0344 |  | 1204.0344 |  | 61.1557 | 2.1808 | 3.8 | 11.3955 | 24.8517 | 6.5399 | OK
| 7/24/2017 6:00 PM | 24 | 1647.1643 |  | 1647.1643 |  | 60.2442 | 2.174 | 4 | 8.3298 | 18.1089 | 4.5272 | OK
| 7/24/2017 7:00 PM | 24 | 1922.7887 |  | 1922.7887 |  | 62.3535 | 2.1603 | 3.8 | 7.1357 | 15.4153 | 4.0567 | OK
| 7/24/2017 8:00 PM | 24 | 1930.359 |  | 1930.359 |  | 61.2759 | 2.1808 | 3.8 | 7.1078 | 15.5009 | 4.0792 | OK
| 7/24/2017 9:00 PM | 24 | 1940.564 |  | 1940.564 |  | 61.4808 | 2.1807 | 3.8 | 7.0704 | 15.4186 | 4.0575 | OK
| 7/24/2017 10:00 PM | 24 | 1926.001 |  | 1926.001 |  | 65.5758 | 2.1877 | 3.4 | 7.1238 | 15.5848 | 4.5838 | OK
| 7/24/2017 11:00 PM | 24 | 1930.6803 |  | 1930.6803 |  | 66.2684 | 2.1739 | 3.2 | 7.1066 | 15.4489 | 4.8278 | OK
| 7/25/2017 12:00 AM | 25 | 2011.8794 |  | 2011.8794 |  | 67.5509 | 2.167 | 3.2 | 6.8198 | 14.7787 | 4.6183 | OK
| 7/25/2017 1:00 AM | 25 | 2045.6096 |  | 2045.6096 |  | 68.1092 | 2.1465 | 3 | 6.7073 | 14.3972 | 4.7991 | OK
| 7/25/2017 2:00 AM | 25 | 2055.4287 |  | 2055.4287 |  | 66.0175 | 2.1533 | 3.4 | 6.6753 | 14.3741 | 4.2277 | OK
| 7/25/2017 3:00 AM | 25 | 2059.2836 |  | 2059.2836 |  | 64.0389 | 2.1601 | 3.6 | 6.6628 | 14.3921 | 3.9978 | OK
| 7/25/2017 4:00 AM | 25 | 2052.5376 |  | 2052.5376 |  | 65.3497 | 2.1602 | 3.4 | 6.6847 | 14.4401 | 4.2471 | OK
| 7/25/2017 5:00 AM | 25 | 2048.7897 |  | 2048.7897 |  | 65.8408 | 2.167 | 3.4 | 6.6969 | 14.5124 | 4.2684 | OK
| 7/25/2017 6:00 AM | 25 | 1438.6146 |  | 1438.6146 |  | 65.7596 | 2.1807 | 3.4 | 9.5373 | 20.7984 | 6.1172 | OK
| 7/25/2017 7:00 AM | 25 | 1128.8642 |  | 1128.8642 |  | 65.6041 | 2.1877 | 3.4 | 12.1543 | 26.5898 | 7.8205 | OK
| 7/25/2017 8:00 AM |  |  |  | 0 |  |  |  | #N/A | #DIV/0! | #DIV/0! | PO | OK
| 7/25/2017 9:00 AM |  |  |  | 0 |  |  |  | #N/A | #DIV/0! | #DIV/0! | PO | OK
| 7/25/2017 10:00 AM |  |  |  | 0 |  |  |  | #N/A | #DIV/0! | #DIV/0! | PO | OK
| 7/25/2017 11:00 AM |  |  |  | 0 |  |  |  | #N/A | #DIV/0! | #DIV/0! | PO | OK
| 7/25/2017 12:00 PM |  |  |  | 0 |  |  |  | #N/A | #DIV/0! | #DIV/0! | PO | OK
| 7/25/2017 1:00 PM | 25 | 1103.0258 |  | 1103.0258 |  | 65.2366 | 2.1942 | 3.4 | 12.439 | 27.2939 | 8.0276 | OK
| 7/25/2017 2:00 PM | 25 | 1117.5885 |  | 1117.5885 |  | 64.8091 | 2.2215 | 3.4 | 12.2769 | 27.2732 | 8.0215 | OK
| 7/25/2017 3:00 PM | 25 | 1419.6616 |  | 1419.6616 |  | 64.9999 | 2.1252 | 3.4 | 9.6646 | 20.5393 | 6.041 | OK
| 7/25/2017 4:00 PM | 25 | 1110.8425 |  | 1110.8425 |  | 64.8339 | 2.1735 | 3.4 | 12.3515 | 26.8454 | 7.8957 | OK
| 7/25/2017 5:00 PM | 25 | 1134.7213 |  | 1134.7213 |  | 64.5477 | 2.1529 | 3.4 | 12.0915 | 26.032 | 7.6565 | OK
| 7/25/2017 6:00 PM | 25 | 1144.3908 |  | 1144.3908 |  | 64.5724 | 2.1665 | 3.4 | 11.9894 | 25.975 | 7.6397 | OK
| 7/25/2017 7:00 PM | 25 | 1130.0421 |  | 1130.0421 |  | 64.3003 | 2.1391 | 3.6 | 12.1416 | 25.9722 | 7.2145 | OK
| 7/25/2017 8:00 PM | 25 | 1146.9608 |  | 1146.9608 |  | 64.053 | 2.1323 | 3.6 | 11.9625 | 25.5072 | 7.0853 | OK
| 7/25/2017 9:00 PM | 25 | 1128.3288 |  | 1128.3288 |  | 63.6573 | 2.1598 | 3.6 | 12.16 | 26.2628 | 7.2952 | OK
| 7/25/2017 10:00 PM | 25 | 1544.7636 |  | 1544.7636 |  | 63.6078 | 2.1185 | 3.6 | 8.882 | 18.816 | 5.2267 | OK
| 7/25/2017 11:00 PM | 25 | 1539.5487 |  | 1539.5487 |  | 63.4665 | 2.1254 | 3.6 | 8.912 | 18.9417 | 5.2616 | OK
| 7/26/2017 12:00 AM | 26 | 1553.1156 |  | 1553.1156 |  | 62.9224 | 2.146 | 3.6 | 8.8342 | 18.9578 | 5.2661 | OK
| 7/26/2017 1:00 AM | 26 | 1536.3043 |  | 1536.3043 |  | 63.6749 | 2.1253 | 3.6 | 8.9309 | 18.9808 | 5.2724 | OK
| 7/26/2017 2:00 AM | 26 | 1514.1386 |  | 1514.1386 |  | 62.9542 | 2.1391 | 3.6 | 9.0616 | 19.3837 | 5.3844 | OK
| 7/26/2017 3:00 AM | 26 | 1545.513 |  | 1545.513 |  | 64.7208 | 2.1391 | 3.4 | 8.8776 | 18.9902 | 5.5854 | OK
| 7/26/2017 4:00 AM | 26 | 1529.0227 |  | 1529.0227 |  | 65.2578 | 2.1461 | 3.4 | 8.9734 | 19.2575 | 5.664 | OK
| 7/26/2017 5:00 AM | 26 | 1536.5184 |  | 1536.5184 |  | 64.6219 | 2.1254 | 3.4 | 8.9296 | 18.9791 | 5.5821 | OK
| 7/26/2017 6:00 AM | 26 | 1130.5775 |  | 1130.5775 |  | 63.311 | 2.1323 | 3.6 | 12.1358 | 25.8768 | 7.188 | OK
| 7/26/2017 7:00 AM | 26 | 1133.3616 |  | 1133.3616 |  | 63.1803 | 2.1872 | 3.6 | 12.106 | 26.4778 | 7.3549 | OK
| 7/26/2017 8:00 AM | 26 | 1108.0585 |  | 1108.0585 |  | 62.8764 | 2.1939 | 3.6 | 12.3825 | 27.1659 | 7.5461 | OK
| 7/26/2017 9:00 AM | 26 | 1114.7724 |  | 1114.7724 |  | 63.0142 | 2.1389 | 3.6 | 12.3079 | 26.3253 | 7.3126 | OK
| 7/26/2017 10:00 AM | 26 | 942.4054 |  | 942.4054 |  | 63.2722 | 2.1871 | 3.6 | 14.559 | 31.8414 | 8.8448 | OK
| 7/26/2017 11:00 AM | 26 | 936.9443 |  | 936.9443 |  | 63.2368 | 2.1665 | 3.6 | 14.6439 | 31.7261 | 8.8128 | OK
| 7/26/2017 12:00 PM | 26 | 942.2984 |  | 942.2984 |  | 63.1591 | 2.1597 | 3.6 | 14.5607 | 31.4461 | 8.735 | OK
| 7/26/2017 1:00 PM | 26 | 938.1222 |  | 938.1222 |  | 62.9754 | 2.201 | 3.6 | 14.6255 | 32.1902 | 8.9417 | OK
| 7/26/2017 2:00 PM | 26 | 952.6102 |  | 952.6102 |  | 62.9789 | 2.1736 | 3.6 | 14.4031 | 31.306 | 8.6961 | OK
| 7/26/2017 3:00 PM | 26 | 967.4943 |  | 967.4943 |  | 62.9506 | 2.1804 | 3.6 | 14.1815 | 30.9216 | 8.5893 | OK
| 7/26/2017 4:00 PM | 26 | 950.897 |  | 950.897 |  | 62.6821 | 2.0155 | 3.6 | 14.429 | 29.0818 | 8.0783 | OK
| 7/26/2017 5:00 PM | 26 | 942.7911 |  | 942.7911 |  | 62.4807 | 2.0018 | 3.8 | 14.5531 | 29.1325 | 7.6665 | OK
| 7/26/2017 6:00 PM | 26 | 949.0766 |  | 949.0766 |  | 62.2157 | 1.9881 | 3.8 | 14.4567 | 28.7416 | 7.5636 | OK
| 7/26/2017 7:00 PM | 26 | 955.5336 |  | 955.5336 |  | 62.0179 | 1.9675 | 3.8 | 14.359 | 28.2508 | 7.4344 | OK
| 7/26/2017 8:00 PM | 26 | 946.935 |  | 946.935 |  | 61.82 | 1.9468 | 3.8 | 14.4894 | 28.208 | 7.4232 | OK
| 7/26/2017 9:00 PM | 26 | 984.9484 |  | 984.9484 |  | 61.6045 | 1.9605 | 3.8 | 13.9302 | 27.3102 | 7.1869 | OK
| 7/26/2017 10:00 PM | 26 | 1550.0106 |  | 1550.0106 |  | 61.1063 | 1.933 | 3.8 | 8.8519 | 17.1107 | 4.5028 | OK
| 7/26/2017 11:00 PM | 26 | 1546.2626 |  | 1546.2626 |  | 61.1981 | 1.9191 | 3.8 | 8.8733 | 17.0287 | 4.4812 | OK
| 7/27/2017 12:00 AM | 27 | 1538.6599 |  | 1538.6599 |  | 61.7458 | 1.9329 | 3.8 | 8.9172 | 17.236 | 4.5358 | OK
| 7/27/2017 1:00 AM | 27 | 1551.1882 |  | 1551.1882 |  | 62.085 | 1.9191 | 3.8 | 8.8452 | 16.9747 | 4.467 | OK
| 7/27/2017 2:00 AM | 27 | 1546.905 |  | 1546.905 |  | 64.3745 | 1.926 | 3.6 | 8.8697 | 17.0834 | 4.7454 | OK
| 7/27/2017 3:00 AM | 27 | 1545.6201 |  | 1545.6201 |  | 64.9716 | 1.9123 | 3.4 | 8.877 | 16.976 | 4.9929 | OK
| 7/27/2017 4:00 AM | 27 | 1544.335 |  | 1544.335 |  | 65.385 | 1.9191 | 3.4 | 8.8844 | 17.05 | 5.0147 | OK
| 7/27/2017 5:00 AM | 27 | 1547.9437 |  | 1547.9437 |  | 66.3637 | 1.9054 | 3.2 | 8.8637 | 16.8888 | 5.2778 | OK
| 7/27/2017 6:00 AM | 27 | 1563.2884 |  | 1563.2884 |  | 66.4238 | 1.9123 | 3.2 | 8.7767 | 16.7841 | 5.245 | OK
| 7/27/2017 7:00 AM | 27 | 1555.7929 |  | 1555.7929 |  | 63.0672 | 1.9946 | 3.6 | 8.819 | 17.5907 | 4.8863 | OK
| 7/27/2017 8:00 AM | 27 | 1549.978 |  | 1549.978 |  | 62.7386 | 2.0359 | 3.6 | 8.8521 | 18.0224 | 5.0062 | OK
| 7/27/2017 9:00 AM | 27 | 959.5705 |  | 959.5705 |  | 62.6008 | 2.0223 | 3.6 | 14.2986 | 28.9153 | 8.032 | OK
| 7/27/2017 10:00 AM | 27 | 952.1819 |  | 952.1819 |  | 62.9824 | 2.0086 | 3.6 | 14.4096 | 28.9423 | 8.0395 | OK
| 7/27/2017 11:00 AM | 27 | 948.402 |  | 948.402 |  | 63.0072 | 2.0086 | 3.6 | 14.467 | 29.0577 | 8.0716 | OK
| 7/27/2017 12:00 PM | 27 | 928.6243 |  | 928.6243 |  | 63.2898 | 1.9742 | 3.6 | 14.7751 | 29.169 | 8.1025 | OK
| 7/27/2017 1:00 PM | 27 | 939.0111 |  | 939.0111 |  | 63.2792 | 1.9537 | 3.6 | 14.6117 | 28.5462 | 7.9295 | OK
| 7/27/2017 2:00 PM | 27 | 946.6137 |  | 946.6137 |  | 63.2368 | 1.9606 | 3.6 | 14.4943 | 28.4177 | 7.8938 | OK
| 7/27/2017 3:00 PM | 27 | 936.7623 |  | 936.7623 |  | 63.1096 | 1.9538 | 3.6 | 14.6467 | 28.6162 | 7.949 | OK
| 7/27/2017 4:00 PM | 27 | 930.873 |  | 930.873 |  | 63.0072 | 1.9538 | 3.6 | 14.7394 | 28.7973 | 7.9992 | OK
| 7/27/2017 5:00 PM | 27 | 947.1813 |  | 947.1813 |  | 62.8623 | 1.9538 | 3.6 | 14.4856 | 28.3015 | 7.8615 | OK
| 7/27/2017 6:00 PM | 27 | 937.0837 |  | 937.0837 |  | 62.5761 | 1.9538 | 3.8 | 14.6417 | 28.6064 | 7.528 | OK
| 7/27/2017 7:00 PM | 27 | 928.6565 |  | 928.6565 |  | 62.4948 | 1.9468 | 3.8 | 14.7746 | 28.7633 | 7.5693 | OK
| 7/27/2017 8:00 PM | 27 | 1396.3826 |  | 1396.3826 |  | 61.9649 | 1.9537 | 3.8 | 9.8258 | 19.1961 | 5.0516 | OK
| 7/27/2017 9:00 PM | 27 | 1445.3929 |  | 1445.3929 |  | 61.6857 | 1.9191 | 3.8 | 9.4926 | 18.2171 | 4.794 | OK
| 7/27/2017 10:00 PM | 27 | 1453.5311 |  | 1453.5311 |  | 61.4313 | 1.9054 | 3.8 | 9.4394 | 17.9858 | 4.7331 | OK
| 7/27/2017 11:00 PM | 27 | 1448.4982 |  | 1448.4982 |  | 61.0992 | 1.8985 | 3.8 | 9.4722 | 17.9834 | 4.7325 | OK
| 7/28/2017 12:00 AM | 28 | 1446.0357 |  | 1446.0357 |  | 63.6573 | 1.8984 | 3.6 | 9.4884 | 18.0131 | 5.0036 | OK
| 7/28/2017 1:00 AM | 28 | 1454.3879 |  | 1454.3879 |  | 64.2862 | 1.8779 | 3.6 | 9.4339 | 17.7158 | 4.921 | OK
| 7/28/2017 2:00 AM | 28 | 1457.4931 |  | 1457.4931 |  | 65.1306 | 1.9053 | 3.4 | 9.4138 | 17.9359 | 5.2753 | OK
| 7/28/2017 3:00 AM | 28 | 1450.747 |  | 1450.747 |  | 65.1836 | 1.8847 | 3.4 | 9.4576 | 17.825 | 5.2427 | OK
| 7/28/2017 4:00 AM | 28 | 1454.0665 |  | 1454.0665 |  | 67.2223 | 1.8916 | 3.2 | 9.436 | 17.8489 | 5.5778 | OK
| 7/28/2017 5:00 AM | 28 | 1444.5366 |  | 1444.5366 |  | 67.5615 | 1.8916 | 3.2 | 9.4982 | 17.9667 | 5.6146 | OK
| 7/28/2017 6:00 AM | 28 | 1451.3573 |  | 1451.3573 |  | 66.9008 | 1.8779 | 3.2 | 9.4536 | 17.7528 | 5.5477 | OK
| 7/28/2017 7:00 AM | 28 | 1452.3532 |  | 1452.3532 |  | 64.9716 | 1.8779 | 3.4 | 9.4471 | 17.7406 | 5.2178 | OK
| 7/28/2017 8:00 AM | 28 | 1427.0824 |  | 1427.0824 |  | 62.4913 | 1.9742 | 3.8 | 9.6144 | 18.9807 | 4.9949 | OK
| 7/28/2017 9:00 AM | 28 | 1432.3293 |  | 1432.3293 |  | 62.1804 | 1.8985 | 3.8 | 9.5792 | 18.1865 | 4.7859 | OK
| 7/28/2017 10:00 AM | 28 | 1424.6195 |  | 1424.6195 |  | 63.1379 | 1.8848 | 3.6 | 9.631 | 18.153 | 5.0425 | OK
| 7/28/2017 11:00 AM | 28 | 1433.5072 |  | 1433.5072 |  | 63.2192 | 1.9123 | 3.6 | 9.5713 | 18.3036 | 5.0843 | OK
| 7/28/2017 12:00 PM | 28 | 1421.4821 |  | 1421.4821 |  | 63.198 | 1.8917 | 3.6 | 9.6523 | 18.2591 | 5.072 | OK
| 7/28/2017 1:00 PM | 28 | 1429.0098 |  | 1429.0098 |  | 62.9012 | 1.8916 | 3.6 | 9.6014 | 18.1619 | 5.045 | OK
| 7/28/2017 2:00 PM | 28 | 1416.7705 |  | 1416.7705 |  | 62.6397 | 1.9123 | 3.6 | 9.6844 | 18.5199 | 5.1444 | OK
| 7/28/2017 3:00 PM | 28 | 1429.5452 |  | 1429.5452 |  | 62.1274 | 1.9605 | 3.8 | 9.5978 | 18.8166 | 4.9517 | OK
| 7/28/2017 4:00 PM | 28 | 1432.8648 |  | 1432.8648 |  | 61.5621 | 1.9675 | 3.8 | 9.5756 | 18.8396 | 4.9578 | OK
| 7/28/2017 5:00 PM | 28 | 1420.4114 |  | 1420.4114 |  | 61.3819 | 1.9812 | 3.8 | 9.6595 | 19.1371 | 5.0361 | OK
| 7/28/2017 6:00 PM |  |  |  | 0 |  |  |  | #N/A | #DIV/0! | #DIV/0! | PO | OK
| 7/28/2017 7:00 PM |  |  |  | 0 |  |  |  | #N/A | #DIV/0! | #DIV/0! | PO | OK
| 7/28/2017 8:00 PM |  |  |  | 0 |  |  |  | #N/A | #DIV/0! | #DIV/0! | PO | OK
| 7/28/2017 9:00 PM | 28 | 914.9181 |  | 914.9181 |  | 61.5939 | 1.9879 | 3.8 | 14.9964 | 29.8114 | 7.8451 | OK
| 7/28/2017 10:00 PM | 28 | 928.4101 |  | 928.4101 |  | 61.1557 | 1.9947 | 3.8 | 14.7785 | 29.4794 | 7.7577 | OK
| 7/28/2017 11:00 PM | 28 | 924.8764 |  | 924.8764 |  | 60.9473 | 1.9947 | 3.8 | 14.835 | 29.592 | 7.7874 | OK
| 7/29/2017 12:00 AM | 29 | 914.5969 |  | 914.5969 |  | 60.3466 | 2.0084 | 4 | 15.0017 | 30.1301 | 7.5325 | OK
| 7/29/2017 1:00 AM | 29 | 924.7694 |  | 924.7694 |  | 60.2159 | 2.0084 | 4 | 14.8367 | 29.7987 | 7.4497 | OK
| 7/29/2017 2:00 AM | 29 | 916.2031 |  | 916.2031 |  | 60.1099 | 2.0084 | 4 | 14.9754 | 30.0773 | 7.5193 | OK
| 7/29/2017 3:00 AM | 29 | 916.3101 |  | 916.3101 |  | 60.0145 | 2.0084 | 4 | 14.9737 | 30.0738 | 7.5184 | OK
| 7/29/2017 4:00 AM | 29 | 939.5465 |  | 939.5465 |  | 59.806 | 2.0223 | 4 | 14.6033 | 29.5316 | 7.3829 | OK
| 7/29/2017 5:00 AM | 29 | 925.0908 |  | 925.0908 |  | 60.6081 | 2.0223 | 4 | 14.8315 | 29.9931 | 7.4983 | OK
| 7/29/2017 6:00 AM | 29 | 939.8356 |  | 939.8356 |  | 62.1097 | 2.0221 | 3.8 | 14.5988 | 29.521 | 7.7687 | OK
| 7/29/2017 7:00 AM | 29 | 951.1112 |  | 951.1112 |  | 62.721 | 2.0221 | 3.6 | 14.4258 | 29.171 | 8.1031 | OK
| 7/29/2017 8:00 AM | 29 | 948.7554 |  | 948.7554 |  | 62.8199 | 2.0359 | 3.6 | 14.4616 | 29.4431 | 8.1786 | OK
| 7/29/2017 9:00 AM | 29 | 964.571 |  | 964.571 |  | 63.3252 | 2.0361 | 3.6 | 14.2245 | 28.9618 | 8.0449 | OK
| 7/29/2017 10:00 AM | 29 | 941.581 |  | 941.581 |  | 63.4594 | 2.0016 | 3.6 | 14.5718 | 29.1668 | 8.1019 | OK
| 7/29/2017 11:00 AM | 29 | 945.4359 |  | 945.4359 |  | 64.0636 | 2.0155 | 3.6 | 14.5124 | 29.2498 | 8.1249 | OK
| 7/29/2017 12:00 PM | 29 | 940.0819 |  | 940.0819 |  | 64.0353 | 1.9949 | 3.6 | 14.595 | 29.115 | 8.0875 | OK
| 7/29/2017 1:00 PM | 29 | 939.8678 |  | 939.8678 |  | 62.6927 | 2.0087 | 3.6 | 14.5983 | 29.3231 | 8.1453 | OK
| 7/29/2017 2:00 PM | 29 | 945.0076 |  | 945.0076 |  | 61.1699 | 2.0018 | 3.8 | 14.5189 | 29.0642 | 7.6485 | OK
| 7/29/2017 3:00 PM | 29 | 939.1182 |  | 939.1182 |  | 60.9897 | 2.0018 | 3.8 | 14.61 | 29.2465 | 7.6964 | OK
| 7/29/2017 4:00 PM | 29 | 942.2235 |  | 942.2235 |  | 61.3253 | 2.0155 | 3.8 | 14.5618 | 29.3495 | 7.7236 | OK
| 7/29/2017 5:00 PM | 29 | 948.038 |  | 948.038 |  | 60.9543 | 2.0155 | 3.8 | 14.4725 | 29.1695 | 7.6762 | OK
| 7/29/2017 6:00 PM | 29 | 943.0052 |  | 943.0052 |  | 60.9579 | 1.995 | 3.8 | 14.5498 | 29.0263 | 7.6385 | OK
| 7/29/2017 7:00 PM | 29 | 942.1164 |  | 942.1164 |  | 61.5585 | 2.0017 | 3.8 | 14.5635 | 29.1518 | 7.6715 | OK
| 7/29/2017 8:00 PM | 29 | 943.8297 |  | 943.8297 |  | 61.7281 | 2.0086 | 3.8 | 14.5371 | 29.1985 | 7.6838 | OK
| 7/29/2017 9:00 PM | 29 | 944.2902 |  | 944.2902 |  | 61.6539 | 2.0154 | 3.8 | 14.53 | 29.2837 | 7.7062 | OK
| 7/29/2017 10:00 PM | 29 | 940.9385 |  | 940.9385 |  | 61.5621 | 2.0086 | 3.8 | 14.5817 | 29.2882 | 7.7074 | OK
| 7/29/2017 11:00 PM | 29 | 936.8694 |  | 936.8694 |  | 61.3465 | 2.0154 | 3.8 | 14.6451 | 29.5157 | 7.7673 | OK
| 7/30/2017 12:00 AM | 30 | 972.5272 |  | 972.5272 |  | 60.9543 | 1.9947 | 3.8 | 14.1081 | 28.1421 | 7.4058 | OK
| 7/30/2017 1:00 AM | 30 | 933.9034 |  | 933.9034 |  | 60.7494 | 1.9665 | 4 | 14.6916 | 28.8909 | 7.2227 | OK
| 7/30/2017 2:00 AM | 30 | 946.2926 |  | 946.2926 |  | 60.276 | 2.0016 | 4 | 14.4992 | 29.0216 | 7.2554 | OK
| 7/30/2017 3:00 AM | 30 | 948.5412 |  | 948.5412 |  | 60.0816 | 2.0016 | 4 | 14.4649 | 28.9528 | 7.2382 | OK
| 7/30/2017 4:00 AM | 30 | 934.8027 |  | 934.8027 |  | 59.6824 | 1.9947 | 4 | 14.6774 | 29.2778 | 7.3195 | OK
| 7/30/2017 5:00 AM | 30 | 941.1527 |  | 941.1527 |  | 59.6859 | 1.9947 | 4 | 14.5784 | 29.0803 | 7.2701 | OK
| 7/30/2017 6:00 AM | 30 | 966.4236 |  | 966.4236 |  | 59.9686 | 1.9879 | 4 | 14.1972 | 28.2226 | 7.0557 | OK
| 7/30/2017 7:00 AM | 30 | 970.2784 |  | 970.2784 |  | 60.5657 | 2.0291 | 4 | 14.1408 | 28.6931 | 7.1733 | OK
| 7/30/2017 8:00 AM | 30 | 922.9492 |  | 922.9492 |  | 61.7811 | 2.0359 | 3.8 | 14.866 | 30.2663 | 7.9648 | OK
| 7/30/2017 9:00 AM | 30 | 941.2598 |  | 941.2598 |  | 62.35 | 2.0291 | 3.8 | 14.5768 | 29.5777 | 7.7836 | OK
| 7/30/2017 10:00 AM | 30 | 954.1094 |  | 954.1094 |  | 63.1944 | 2.0565 | 3.6 | 14.3804 | 29.5733 | 8.2148 | OK
| 7/30/2017 11:00 AM | 30 | 965.1386 |  | 965.1386 |  | 63.6078 | 2.0635 | 3.6 | 14.2161 | 29.3342 | 8.1484 | OK
| 7/30/2017 12:00 PM | 30 | 980.1299 |  | 980.1299 |  | 64.0353 | 2.0362 | 3.6 | 13.9987 | 28.5036 | 7.9177 | OK
| 7/30/2017 1:00 PM | 30 | 936.3341 |  | 936.3341 |  | 64.3887 | 2.0567 | 3.6 | 14.6534 | 30.1379 | 8.3716 | OK
| 7/30/2017 2:00 PM | 30 | 946.2926 |  | 946.2926 |  | 64.5265 | 2.0018 | 3.4 | 14.4992 | 29.0247 | 8.5367 | OK
| 7/30/2017 3:00 PM | 30 | 941.9023 |  | 941.9023 |  | 64.7314 | 1.9813 | 3.4 | 14.5668 | 28.8607 | 8.4884 | OK
| 7/30/2017 4:00 PM | 30 | 943.2943 |  | 943.2943 |  | 64.9045 | 2.0088 | 3.4 | 14.5453 | 29.2182 | 8.5936 | OK
| 7/30/2017 5:00 PM | 30 | 952.4283 |  | 952.4283 |  | 64.8409 | 2.0225 | 3.4 | 14.4058 | 29.1353 | 8.5692 | OK
| 7/30/2017 6:00 PM | 30 | 943.5084 |  | 943.5084 |  | 64.8586 | 2.0293 | 3.4 | 14.542 | 29.5103 | 8.6795 | OK
| 7/30/2017 7:00 PM | 30 | 935.7987 |  | 935.7987 |  | 64.6713 | 2.0155 | 3.4 | 14.6618 | 29.551 | 8.6915 | OK
| 7/30/2017 8:00 PM |  |  |  | 0 |  |  |  | #N/A | #DIV/0! | #DIV/0! | PO | OK
| 7/30/2017 9:00 PM |  |  |  | 0 |  |  |  | #N/A | #DIV/0! | #DIV/0! | PO | OK
| 7/30/2017 10:00 PM | 30 | 908.0649 |  | 908.0649 |  | 64.4593 | 2.0086 | 3.4 | 15.1096 | 30.3485 | 8.926 | OK
| 7/30/2017 11:00 PM | 30 | 960.213 |  | 960.213 |  | 64.212 | 2.0086 | 3.6 | 14.289 | 28.7003 | 7.9723 | OK
| 7/31/2017 12:00 AM | 31 | 943.5084 |  | 943.5084 |  | 63.6537 | 2.0154 | 3.6 | 14.542 | 29.308 | 8.1411 | OK
| 7/31/2017 1:00 AM | 31 | 940.4032 |  | 940.4032 |  | 63.5372 | 2.0362 | 3.6 | 14.59 | 29.7077 | 8.2521 | OK
| 7/31/2017 2:00 AM | 31 | 946.0784 |  | 946.0784 |  | 63.0849 | 2.043 | 3.6 | 14.5025 | 29.6288 | 8.2302 | OK
| 7/31/2017 3:00 AM | 31 | 940.0819 |  | 940.0819 |  | 62.3252 | 2.0565 | 3.8 | 14.595 | 30.0146 | 7.8986 | OK
| 7/31/2017 4:00 AM | 31 | 949.7191 |  | 949.7191 |  | 62.0991 | 2.043 | 3.8 | 14.4469 | 29.5152 | 7.7672 | OK
| 7/31/2017 5:00 AM | 31 | 954.3234 |  | 954.3234 |  | 61.3006 | 2.0498 | 3.8 | 14.3772 | 29.4697 | 7.7552 | OK
| 7/31/2017 6:00 AM | 31 | 950.0403 |  | 950.0403 |  | 60.7954 | 2.0566 | 4 | 14.442 | 29.7015 | 7.4254 | OK
| 7/31/2017 7:00 AM | 31 | 939.8356 |  | 939.8356 |  | 60.3325 | 2.0978 | 4 | 14.5988 | 30.6255 | 7.6564 | OK
| 7/31/2017 8:00 AM | 31 | 928.1959 |  | 928.1959 |  | 60.1452 | 2.084 | 4 | 14.7819 | 30.8055 | 7.7014 | OK
| 7/31/2017 9:00 AM | 31 | 968.5652 |  | 968.5652 |  | 60.4385 | 2.0841 | 4 | 14.1658 | 29.523 | 7.3808 | OK
| 7/31/2017 10:00 AM | 31 | 1438.4007 |  | 1438.4007 |  | 61.2829 | 2.0771 | 3.8 | 9.5387 | 19.8134 | 5.214 | OK
| 7/31/2017 11:00 AM | 31 | 1458.564 |  | 1458.564 |  | 61.6363 | 2.1254 | 3.8 | 9.4069 | 19.9935 | 5.2614 | OK
| 7/31/2017 12:00 PM | 31 | 1462.6331 |  | 1462.6331 |  | 63.2969 | 2.1598 | 3.6 | 9.3807 | 20.2601 | 5.6278 | OK
| 7/31/2017 1:00 PM | 31 | 1457.172 |  | 1457.172 |  | 64.4664 | 2.1874 | 3.4 | 9.4159 | 20.596 | 6.0576 | OK
| 7/31/2017 2:00 PM | 31 | 1394.7442 |  | 1394.7442 |  | 64.6537 | 2.1668 | 3.4 | 9.8373 | 21.3157 | 6.2693 | OK
| 7/31/2017 3:00 PM | 31 | 940.9385 |  | 940.9385 |  | 65.1306 | 2.1462 | 3.4 | 14.5817 | 31.2949 | 9.2044 | OK
| 7/31/2017 4:00 PM | 31 | 943.2943 |  | 943.2943 |  | 65.3744 | 2.1255 | 3.4 | 14.5453 | 30.9163 | 9.093 | OK
| 7/31/2017 5:00 PM | 31 | 930.3375 |  | 930.3375 |  | 64.7844 | 2.1117 | 3.4 | 14.7479 | 31.1433 | 9.1598 | OK
| 7/31/2017 6:00 PM | 31 | 944.258 |  | 944.258 |  | 63.8481 | 2.0911 | 3.6 | 14.5305 | 30.3841 | 8.44 | OK
| 7/31/2017 7:00 PM | 31 | 935.3703 |  | 935.3703 |  | 63.4842 | 2.0773 | 3.6 | 14.6685 | 30.4703 | 8.464 | OK
| 7/31/2017 8:00 PM | 31 | 912.6694 |  | 912.6694 |  | 63.0425 | 2.0637 | 3.6 | 15.0334 | 31.0239 | 8.6177 | OK
| 7/31/2017 9:00 PM | 31 | 945.361 |  | 945.361 |  | 63.8834 | 2.0774 | 3.6 | 14.5135 | 30.1498 | 8.375 | OK
| 7/31/2017 10:00 PM | 31 | 936.8694 |  | 936.8694 |  | 62.6008 | 2.0566 | 3.6 | 14.6451 | 30.1191 | 8.3664 | OK
| 7/31/2017 11:00 PM | 31 | 945.3289 |  | 945.3289 |  | 61.5727 | 2.0566 | 3.8 | 14.514 | 29.8495 | 7.8551 | OK
NOTES, CALCULATIONS, AND ASSUMPTIONS
Park Meadows must obtain 4 log removal credit for virus from chlorine disinfection prior to the first customer.
Yellow fields are for input.
Compliance ratio must be greater than 1.0 ninety-five percent of the time on a monthly basis.
Required CTr for 4 log removal taken from Table C-7, EPA Guidance Manual Disinfection Profiling and Benchmarking
Sequence 1 Time = (Volume in Pipeline to Boothill Tank) / (Flow in gpm) * (T10/T ratio)
CTa = (time) * (chlorine concentration)
The pipeline volume is 13,721 gallons based on 2335.3 ft of 12" pipe from the Creekside WTP to the chlorine analyzer upstream of Boothill Tank.
[9 empty] | Volume |  | T10/T
[9 empty] | (Gals) |  | (-)
| Sequence 1: Pipeline from Creekside WTP to Boothill Tank | [7 empty] | 13720.5164 |  | 1
Required CTr for 4 log removal taken from Table C-7, EPA Guidance Manual Disinfection Profiling and Benchmarking
| Temp (Deg F) |  | 32.9 | 33.8 | 35.6 | 37.4 | 39.2 | 41 | 42.8 | 44.6 | 46.4 | 48.2 | 50 | 51.8 | 53.6 | 55.4 | 57.2 | 59 | 60.8 | 62.6 | 64.4 | 66.2 | 68
| Temp (Deg C) |  | 0.5 | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16 | 17 | 18 | 19 | 20
| Req'd CTr (mg-min/L) |  | 12 | 11.6 | 10.7 | 9.8 | 8.9 | 8 | 7.6 | 7.2 | 6.8 | 6.4 | 6 | 5.6 | 5.2 | 4.8 | 4.4 | 4 | 3.8 | 3.6 | 3.4 | 3.2 | 3

## DISINFECTION REPORT
Monthly Report for Water Treatment Technique Compliance - Disinfection
| Month: | July |  |  | Utility Name: | Park City |  |  | Conventional
| Year: | 2017 |  |  | Treatment Plant: | Creekside Water Treatment Plant |  |  | Direct Filtration
| System Number: | 22011 |  |  | Filtration Technology: | Cartridge Filtration |  |  | Membrane Filtration
[5 empty] | Prepared by: | Iwona Goodley |  |  | Slow Sand Filtration
Cartridge Filtration
D. | Record the daily minimum disinfectant residual at the point-of-entry (POE) to the distribution system | [7 empty] | Bag Filtration
| and the minimum daily plant total inactivation ratio (CTprovided/CTrequired). | [7 empty] | Diatomaceous Earth Filtration
Other (attach description)
|  | Min POE |  |  |  | Min POE |  |  | None
|  | Cl2 Res | Total Inactivation |  |  | Cl2 Res | Total Inactivation
| Date | (mg/L) | Ratio |  | Date | (mg/L) | Ratio
| 7/1 | 1.9062 | #N/A |  | 7/16 | 2.0297 | #N/A
| 7/2 | 1.98 | #N/A |  | 7/17 | 2.0159 | #N/A
| 7/3 | 2.0434 | #N/A |  | 7/18 | 1.8856 | #N/A
| 7/4 | 1.7691 | #N/A |  | 7/19 | 1.865 | #N/A
| 7/5 | 1.6866 | #N/A |  | 7/20 |  | #N/A
| 7/6 | 1.9541 | PO |  | 7/21 | 1.8238 | #N/A
| 7/7 | 1.6594 | PO |  | 7/22 | 1.5 | #N/A
| 7/8 | 1.9541 | PO |  | 7/23 | 1.0141 | #N/A
| 7/9 | 1.92 | PO |  | 7/24 | 1.9 | #N/A
| 7/10 | 1.7622 | PO |  | 7/25 | 1.83 | #N/A
| 7/11 | 1.9 | #N/A |  | 7/26 |  | #N/A
| 7/12 | 1.9131 | #N/A |  | 7/27 | 1.87 | #N/A
| 7/13 | 1.98 | #N/A |  | 7/28 | 1.7759 | #N/A
| 7/14 | 1.9541 | #N/A |  | 7/29 | 1.7553 | #N/A
| 7/15 | 1.9678 | #N/A |  | 7/30 | 2.02 | #N/A
[5 empty] | 7/31 | 1.275 | #N/A
E. | Record the date of occurrence, duration and date reported for each time the disinfectant residual
was less than 0.2 mg/L or the total Inactivation Ratio was less than 1. Attach details of public
notice for each event. If none, enter "none".
Pertinent Residual or
| Date |  | Duration | Total Inactivation |  | Date Reported | Date of Public
|  |  | (Hours) | Ratio Value |  | to State | Notice
None
F. | Distribution System Disinfectant Residual Criteria
[6 empty] | Number of sites where disinfectant residual measurements were made | A = | 13
[6 empty] | Number of sites where HPC samples were taken instead of residual measurements | B = | 0
[6 empty] | Number of sites where no residual was detected and no HPC sample was taken | C = | 0
[6 empty] | Number of sites where no residual was detected and HPC exceeded 500 | D = | 0
[6 empty] | Number of sites where no residual measurement was made and HPC exceeded 500 | E = | 0
| Violation percentage for this month* |  |  | 0 | Violation percentage for last month* |  |  | 0
Violation percentage = 100x(C+D+E)/(A+B)

## SEQUENCE 1
FIRST DISINFECTION SEQUENCE | [11 empty] | 65.3651 | -25.1799 | 5.3729 | 0.13583 | -21.0607 | 8.7299 | -1.1983 | 0.053508
| Month: | July |  |  | Utility Name: | Park City
| Year: | 2017 |  |  | Treatment Plant: | Creekside Water Treatment Plant
| System Number: | 22011 |  |  | Prepared by: | Iwona Goodley | [5 empty] | -204.2399 | 169.0885 | -35.8183 | 2.3157 | 40.0957 | -16.7906 | 2.3238 | -0.10631
[12 empty] | 162.8669 | -110.8682 | 21.5511 | -1.2712 | -22.277 | 9.3493 | -1.2972 | 0.059385
[7 empty] | Giardia Log Inactivation Treatment Credit granted by Utah DDW: | 2.5 |  |  |  | -624.0289 | 260.5181 | -36.1906 | 1.6036 | 0.94149 | -0.38955 | 0.053357 | -0.0023787
[7 empty] | Required Giardia Log Inactivation for UV Disinfection: | 0.5
[7 empty] | Required Giardia Log Inactivation for Chlorine Disinfection: | None
[7 empty] | Crypto Log Inactivation Treatment Credit granted by Utah DDW: | 2
[7 empty] | Required Crypto Log Inactivation for UV Disinfection: | 3.5
[7 empty] | Required Crypto Log Inactivation for Chlorine Disinfection: | None
[7 empty] | Virus Log Inactivation Treatment Credit granted by Utah DDW: | 0 |  |  |  | 1141.9863 | -489.7483 | 69.4313 | -3.258 | -1.7929 | 0.74862 | -0.10331 | 0.0047132
[7 empty] | Required Virus Log Inactivation for UV Disinfection: | None
[7 empty] | Required Virus Log Inactivation for Chlorine Disinfection (see table below): | 4 |  |  |  | -599.3181 | 259.4069 | -37.1033 | 1.7463 | 1.0001 | -0.4181 | 0.057795 | -0.002637
| Inactivation Ratio Calculation - All data for the same point in time, and at the end of the sequence. | [10 empty] | 97.7448 | -42.7328 | 6.1666 | -0.29213 | -0.16736 | 0.070161 | -0.0097272 | 0.00044499
|  | Diameter = | 12 | in. | Length = | 2335.333 | ft. |  |  |  |  | 193.2259 | -80.3113 | 11.0611 | -0.49461 | -0.014746 | 0.0060931 | -0.00083331 | 3.7096e-05
|  | Peak Daily | Peak Flow | Peak Flow Cl2 |  |  |  |  | Inactivation |  |  |  | -364.4075 | 153.4256 | -21.3486 | 0.98198 | 0.027982 | -0.011662 | 0.0016063 | -7.3152e-05
| Date | Flow (PM & Divide) | Detention Time | Residual |  | Temperature | CT Provided | CT Required | Ratio |  |  |  | 199.4472 | -84.3243 | 11.7853 | -0.54307 | -0.015597 | 0.0065043 | -0.00089704 | 4.0845e-05
|  | (gpm) | (Minutes) | (mg/l) | pH | (Deg C) | (min.*mg/L) | (min.*mg/L) | Provided | Cl2 | pH | Temp | -33.2159 | 14.1164 | -1.9828 | 0.09174 | 0.0026014 | -0.0010874 | 0.00015037 | -6.8638e-06
| 1 | #N/A | #N/A | 1.25 | #N/A | #N/A | #N/A | #N/A | #N/A | 1.25 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #REF! | #REF! | #REF! | #REF!
| 2 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #REF! | #REF! | #REF! | #REF!
| 3 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #REF! | #REF! | #REF! | #REF!
| 4 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #REF! | #REF! | #REF! | #REF!
| 5 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #REF! | #REF! | #REF! | #REF!
| 6 | PO | PO | PO | PO | PO | PO |  |  | 3 | 9 | 25 | -78.6643 | 294.9548 | -341.0624 | 189.1888 | -9.2168 | 323.0829 | -764.1573 | 495.2188 | 922.6816 | -3706.8846 | 4878.5536 | -2111.988 | #REF! | #REF! | #REF! | #REF!
| 7 | PO | PO | PO | PO | PO | PO |  |  | 3 | 9 | 25 | -78.6643 | 294.9548 | -341.0624 | 189.1888 | -9.2168 | 323.0829 | -764.1573 | 495.2188 | 922.6816 | -3706.8846 | 4878.5536 | -2111.988 | #REF! | #REF! | #REF! | #REF!
| 8 | PO | PO | PO | PO | PO | PO |  |  | 3 | 9 | 25 | -78.6643 | 294.9548 | -341.0624 | 189.1888 | -9.2168 | 323.0829 | -764.1573 | 495.2188 | 922.6816 | -3706.8846 | 4878.5536 | -2111.988 | #REF! | #REF! | #REF! | #REF!
| 9 | PO | PO | PO | PO | PO | PO |  |  | 3 | 9 | 25 | -78.6643 | 294.9548 | -341.0624 | 189.1888 | -9.2168 | 323.0829 | -764.1573 | 495.2188 | 922.6816 | -3706.8846 | 4878.5536 | -2111.988 | #REF! | #REF! | #REF! | #REF!
| 10 | PO | PO | PO | PO | PO | PO |  |  | 3 | 9 | 25 | -78.6643 | 294.9548 | -341.0624 | 189.1888 | -9.2168 | 323.0829 | -764.1573 | 495.2188 | 922.6816 | -3706.8846 | 4878.5536 | -2111.988 | #REF! | #REF! | #REF! | #REF!
| 11 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #REF! | #REF! | #REF! | #REF!
| 12 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #REF! | #REF! | #REF! | #REF!
| 13 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #REF! | #REF! | #REF! | #REF!
| 14 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #REF! | #REF! | #REF! | #REF!
| 15 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #REF! | #REF! | #REF! | #REF!
| 16 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #REF! | #REF! | #REF! | #REF!
| 17 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #REF! | #REF! | #REF! | #REF!
| 18 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #REF! | #REF! | #REF! | #REF!
| 19 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #REF! | #REF! | #REF! | #REF!
| 20 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #REF! | #REF! | #REF! | #REF!
| 21 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #REF! | #REF! | #REF! | #REF!
| 22 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #REF! | #REF! | #REF! | #REF!
| 23 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #REF! | #REF! | #REF! | #REF!
| 24 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #REF! | #REF! | #REF! | #REF!
| 25 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #REF! | #REF! | #REF! | #REF!
| 26 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #REF! | #REF! | #REF! | #REF!
| 27 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #REF! | #REF! | #REF! | #REF!
| 28 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #REF! | #REF! | #REF! | #REF!
| 29 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #REF! | #REF! | #REF! | #REF!
| 30 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #REF! | #REF! | #REF! | #REF!
| 31 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #REF! | #REF! | #REF! | #REF!
| AVG | [6 empty] | #N/A
| MAX | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
| MIN | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
Note on I6: Michelle DeHaan: Let's talk through this in depth since this is the meat of the report to me. UWQA Inactivation Goal = 2.

## CT Description
This page provides a brief explanation of the CT reporting tabs in this Excel file, specifically the “Operational Worksheet,” “Disinfection Report,” and “Sequence 1” tabs.
Background:
Utah DDW reporting typically utilizes readings taken every 4 hours (6 readings per day). Utah DDW guidelines are based on reporting daily CT performance as the inactivation ratio from the 4-hr increment with the highest (peak) flow.
The intent of using the peak flow is to capture the worst-case condition for CT (i.e. the lowest activation ratio) based on an inherent assumption that the worst case will occur when the flows are highest and detention times lowest.
CT calculations are based on measured water temperature, flow rate in the combined Park Meadows and Divide pipeline, measured chlorine residual, and volume of water in the pipeline from the Creekside WTP to Boothill Tank.
Similar to the Quinns Junction WTP, CT reporting for the Creekside WTP uses an hourly calculated CT ratio of actual to required CT using the variables listed in item 3 and reports data at the lowest CT ratio.
“Operational Worksheet” Tab:
The purpose of this worksheet is to provide hourly CT calculations for each day of the month, including CTr, CTa, and inactivation (CT) ratio. It also identifies which hour of each day has the lowest inactivation ratio for reporting purposes, and it provides information to the “Sequence 1” tab.
This tab has cells populated by the plant SCADA system. These cells are highlighted yellow and include hourly data for Park Meadows flow rate, Divide flow rate, raw water temperature, and chlorine residual at the chlorine analyzer near Boothill Tank.
Calculations are described in the “Notes, Calculations, and Assumptions” section below the main table.
At the bottom of the worksheet is the lookup table for CTr for 3.5-log virus removal based on temperature. Note that this table is evaluated conservatively. Where a temperature is between values, the CTr for the lower temperature (the higher CTr) is used.
This tab could have been used to directly provide the required information into the “Disinfection Report” tab. However, Utah DDW uses separate tabs for each sequence, so we have preserved that format.
“Sequence 1” Tab:
The purpose of this tab is to provide the daily inactivation ratio, which is based on the data from the hour with the lowest total inactivation ratio identified in the “Operational Worksheet” tab. This tab provides the inactivation (CT) ratio for the “Disinfection Report” tab.
Terminology in this tab was based on terminology in the Utah DDW spreadsheets. Although the table references “peak flow,” the actual condition used is the lowest inactivation ratio for that day (as explained above).
The detention time, chlorine residual, temperature, and CTr are referenced into this tab from the “Operational Worksheet” tab.
pH is not used because it is only required for Giardia and Crypo inactivation, and no additional inactivation is required through chlorine application.
“Disinfection Report” Tab”
This tab is the official disinfection report for Utah DDW. The inactivation ratio for each day is the worst-case inactivation ratio for each day as shown in the “Sequence 1” tab.
Note on M2: Michelle DeHaan: I like this description page a lot. Thinking we need to expand it to capture calcs discussed earlier.