## EPA Monthly Summary
LT1SWTR MONTHLY REPORT TO EPA FOR COMPLIANCE DETERMINATION
MEMBRANE FILTRATION SYSTEMS (MF, UL, RO)
(Due to EPA by 10th day of the following month)
Month |  |  |  | 11 | [5 empty] | System/Treatment Plant | [10 empty] | Quinn's Water Treatment Plant | [21 empty] | PWSID |  |  |  | 22011
Year |  |  |  | 2015 | [5 empty] | Type of Filtration | [10 empty] | Membrane Filtration
Combined Effluent Turbidity Performance Criteria (DATA ON PAGE 2)
A. Total number of Combined Filter Effluent (CFE) water turbidity measurements = | [37 empty] | 180
B. Total Number of CFE water turbidity measurements that are less than or equal to 0.3 NTU = | [43 empty] | 180
C. The percentage of CFE turbidity measurements meeting 0.3 NTU = B / A * 100 = | [38 empty] | 100 | [5 empty] | %
D. Record the date and turbidity value for any CFE measurements exceeding 1 NTU: If none, enter “none” below:
E. Total number of chlorine residual measurements: | [24 empty] | 31
|  |  |  | Time and Date of Exceedance | [15 empty] | Highest Trubidity (NTU) | [11 empty] | Time and Date EPA Was Notified
Disinfection Performance Criteria
A. Point-of-Entry Minimum Disinfectant Residual Criteria and CT Criteria
The minimum residual concentration must not drop below 0.2 mg/L OR the higher value (>0.2 mg/L) needed each day for adequate inactivation of Giardia and viruses.
Date |  |  |  | Minimum Disinfectant Residual at Point of Entry to Distribution System (mg/L) | [14 empty] | Date |  |  | Minimum Disinfectant Residual at Point of Entry to Distribution System (mg/L) | [14 empty] | Date |  | Minimum Disinfectant Residual at Point of Entry to Distribution System (mg/L)
2015-11-01 | 2015-11-01 | 2015-11-01 | 2015-11-01 | 2.2286 | 2.2286 | 2.2286 | 2.2286 | 2.2286 | 2.2286 | 2.2286 | 2.2286 | 2.2286 | 2.2286 | 2.2286 | 2.2286 | 2.2286 | 2.2286 | 2.2286 | 2015-11-11 |  |  | 2.4898 | 2.4898 | 2.4898 | 2.4898 | 2.4898 | 2.4898 | 2.4898 | 2.4898 | 2.4898 | 2.4898 | 2.4898 | 2.4898 | 2.4898 | 2.4898 | 2.4898 | 2015-11-21 |  | 2.1669 | 2.1669 | 2.1669 | 2.1669 | 2.1669 | 2.1669 | 2.1669 | 2.1669 | 2.1669 | 2.1669 | 2.1669 | 2.1669 | 2.1669 | 2.1669 | 2.1669
2015-11-02 |  |  |  | 2.2904 | 2.2904 | 2.2904 | 2.2904 | 2.2904 | 2.2904 | 2.2904 | 2.2904 | 2.2904 | 2.2904 | 2.2904 | 2.2904 | 2.2904 | 2.2904 | 2.2904 | 2015-11-12 |  |  | 2.5103 | 2.5103 | 2.5103 | 2.5103 | 2.5103 | 2.5103 | 2.5103 | 2.5103 | 2.5103 | 2.5103 | 2.5103 | 2.5103 | 2.5103 | 2.5103 | 2.5103 | 2015-11-22 |  | 2.359 | 2.359 | 2.359 | 2.359 | 2.359 | 2.359 | 2.359 | 2.359 | 2.359 | 2.359 | 2.359 | 2.359 | 2.359 | 2.359 | 2.359
2015-11-03 |  |  |  | 2.0158 | 2.0158 | 2.0158 | 2.0158 | 2.0158 | 2.0158 | 2.0158 | 2.0158 | 2.0158 | 2.0158 | 2.0158 | 2.0158 | 2.0158 | 2.0158 | 2.0158 | 2015-11-13 |  |  | 2.4833 | 2.4833 | 2.4833 | 2.4833 | 2.4833 | 2.4833 | 2.4833 | 2.4833 | 2.4833 | 2.4833 | 2.4833 | 2.4833 | 2.4833 | 2.4833 | 2.4833 | 2015-11-23 |  | 2.1878 | 2.1878 | 2.1878 | 2.1878 | 2.1878 | 2.1878 | 2.1878 | 2.1878 | 2.1878 | 2.1878 | 2.1878 | 2.1878 | 2.1878 | 2.1878 | 2.1878
2015-11-04 |  |  |  | 2.2287 | 2.2287 | 2.2287 | 2.2287 | 2.2287 | 2.2287 | 2.2287 | 2.2287 | 2.2287 | 2.2287 | 2.2287 | 2.2287 | 2.2287 | 2.2287 | 2.2287 | 2015-11-14 |  |  | 2.2217 | 2.2217 | 2.2217 | 2.2217 | 2.2217 | 2.2217 | 2.2217 | 2.2217 | 2.2217 | 2.2217 | 2.2217 | 2.2217 | 2.2217 | 2.2217 | 2.2217 | 2015-11-24 |  | 2.373 | 2.373 | 2.373 | 2.373 | 2.373 | 2.373 | 2.373 | 2.373 | 2.373 | 2.373 | 2.373 | 2.373 | 2.373 | 2.373 | 2.373
2015-11-05 |  |  |  | 2.2493 | 2.2493 | 2.2493 | 2.2493 | 2.2493 | 2.2493 | 2.2493 | 2.2493 | 2.2493 | 2.2493 | 2.2493 | 2.2493 | 2.2493 | 2.2493 | 2.2493 | 2015-11-15 |  |  | 2.3591 | 2.3591 | 2.3591 | 2.3591 | 2.3591 | 2.3591 | 2.3591 | 2.3591 | 2.3591 | 2.3591 | 2.3591 | 2.3591 | 2.3591 | 2.3591 | 2.3591 | 2015-11-25 |  | 2.2427 | 2.2427 | 2.2427 | 2.2427 | 2.2427 | 2.2427 | 2.2427 | 2.2427 | 2.2427 | 2.2427 | 2.2427 | 2.2427 | 2.2427 | 2.2427 | 2.2427
2015-11-06 |  |  |  | 2.2835 | 2.2835 | 2.2835 | 2.2835 | 2.2835 | 2.2835 | 2.2835 | 2.2835 | 2.2835 | 2.2835 | 2.2835 | 2.2835 | 2.2835 | 2.2835 | 2.2835 | 2015-11-16 |  |  | 2.4074 | 2.4074 | 2.4074 | 2.4074 | 2.4074 | 2.4074 | 2.4074 | 2.4074 | 2.4074 | 2.4074 | 2.4074 | 2.4074 | 2.4074 | 2.4074 | 2.4074 | 2015-11-26 |  | 2.2358 | 2.2358 | 2.2358 | 2.2358 | 2.2358 | 2.2358 | 2.2358 | 2.2358 | 2.2358 | 2.2358 | 2.2358 | 2.2358 | 2.2358 | 2.2358 | 2.2358
2015-11-07 |  |  |  | 2.304 | 2.304 | 2.304 | 2.304 | 2.304 | 2.304 | 2.304 | 2.304 | 2.304 | 2.304 | 2.304 | 2.304 | 2.304 | 2.304 | 2.304 | 2015-11-17 |  |  | 2.4625 | 2.4625 | 2.4625 | 2.4625 | 2.4625 | 2.4625 | 2.4625 | 2.4625 | 2.4625 | 2.4625 | 2.4625 | 2.4625 | 2.4625 | 2.4625 | 2.4625 | 2015-11-27 |  | 2.3522 | 2.3522 | 2.3522 | 2.3522 | 2.3522 | 2.3522 | 2.3522 | 2.3522 | 2.3522 | 2.3522 | 2.3522 | 2.3522 | 2.3522 | 2.3522 | 2.3522
2015-11-08 |  |  |  | 2.0639 | 2.0639 | 2.0639 | 2.0639 | 2.0639 | 2.0639 | 2.0639 | 2.0639 | 2.0639 | 2.0639 | 2.0639 | 2.0639 | 2.0639 | 2.0639 | 2.0639 | 2015-11-18 |  |  | 2.6069 | 2.6069 | 2.6069 | 2.6069 | 2.6069 | 2.6069 | 2.6069 | 2.6069 | 2.6069 | 2.6069 | 2.6069 | 2.6069 | 2.6069 | 2.6069 | 2.6069 | 2015-11-28 |  | 2.2975 | 2.2975 | 2.2975 | 2.2975 | 2.2975 | 2.2975 | 2.2975 | 2.2975 | 2.2975 | 2.2975 | 2.2975 | 2.2975 | 2.2975 | 2.2975 | 2.2975
2015-11-09 |  |  |  | 2.2356 | 2.2356 | 2.2356 | 2.2356 | 2.2356 | 2.2356 | 2.2356 | 2.2356 | 2.2356 | 2.2356 | 2.2356 | 2.2356 | 2.2356 | 2.2356 | 2.2356 | 2015-11-19 |  |  | 2.3731 | 2.3731 | 2.3731 | 2.3731 | 2.3731 | 2.3731 | 2.3731 | 2.3731 | 2.3731 | 2.3731 | 2.3731 | 2.3731 | 2.3731 | 2.3731 | 2.3731 | 2015-11-29 |  | 2.0843 | 2.0843 | 2.0843 | 2.0843 | 2.0843 | 2.0843 | 2.0843 | 2.0843 | 2.0843 | 2.0843 | 2.0843 | 2.0843 | 2.0843 | 2.0843 | 2.0843
2015-11-10 |  |  |  | 2.2015 | 2.2015 | 2.2015 | 2.2015 | 2.2015 | 2.2015 | 2.2015 | 2.2015 | 2.2015 | 2.2015 | 2.2015 | 2.2015 | 2.2015 | 2.2015 | 2.2015 | 2015-11-20 |  |  | 2.3522 | 2.3522 | 2.3522 | 2.3522 | 2.3522 | 2.3522 | 2.3522 | 2.3522 | 2.3522 | 2.3522 | 2.3522 | 2.3522 | 2.3522 | 2.3522 | 2.3522 | 2015-11-30 |  | 2.4966 | 2.4966 | 2.4966 | 2.4966 | 2.4966 | 2.4966 | 2.4966 | 2.4966 | 2.4966 | 2.4966 | 2.4966 | 2.4966 | 2.4966 | 2.4966 | 2.4966
Days where the POE Residual Was < 0.2 mg/L for > 4 hours
Time/Day | [18 empty] | Duration of Low Level (indicate hrs) | [17 empty] | Time and Date Reported to EPA
B. Distribution System Disinfectant Residual Criteria MEASURED WHEN TAKING TCR (BACT) SAMPLES
A = # of samples this month that disinfectant residual was measured in distribution system = | [45 empty] | 0
C = # of samples this month that disinfectant residual was NOT detected when you measured = | [45 empty] | 0
V = C / A * 100 = | [11 empty] | #DIV/0! | [7 empty] | % |  |  | For the previous month, V = | [13 empty] | ____________ | [5 empty] | %
Prepared by | [6 empty] | ____________________________________________________________ | [32 empty] | Date |  |  | __________________
Formulas:
Year = [Year, row above]+1

## Turbidity Daily Data Sheet
MONTHLY REPORTING SHEET FOR COMBINED FILTER EFFLUENT (CFE) TURBIDITY
MEMBRANE FILTRATION SYSTEMS (MF, UL, RO)
Month | 11 | System Treatment Plant: |  | Quinn's Water Treatment Plant
Year Filtration Technology: | 2015 | PWS ID#: |  | 22011
REQUIRED # OF 4-HOUR TURBIDITY READINGS/DAY = |  |  |  | 6 | (UNLESS PLANT OFF – INDICATE “PO” IN EACH CELL)
**REPORT MAXIMUM TURBIDITY READING THAT DAY, EVEN IF IT WAS BETWEEN 4 HOUR READINGS
DO NOT REPORT RESULTS COLLECTED DURING BACKWASH, FILTER-TO-WASTE, OR ANY TIME WATER IS NOT BEING PRODUCED FOR CONSUMPTION
Date | 1200 AM (NTU) | 4 AM (NTU) | 8 AM (NTU) | 12 PM (NTU) | 4 PM (NTU) | 8 PM (NTU ) | **DAILY Max NTU
2015-11-01 | 0.010243 | 0.010225 | 0.010186 | 0.010255 | 0.010255 | 0.010225 | 0.010255
2015-11-02 | 0.010628 | 0.011187 | 0.012826 | 0.010588 | 0.010588 | 0.010304 | 0.012826
2015-11-03 | 0.010304 | 0.010166 | 0.010392 | 0.011992 | 0.01049 | 0.014377 | 0.014377
2015-11-04 | 0.01261 | 0.01051 | 0.011894 | 0.010323 | 0.010608 | 0.010608 | 0.01261
2015-11-05 | 0.010608 | 0.010333 | 0.010333 | 0.010294 | 0.010421 | 0.010421 | 0.010608
2015-11-06 | 0.010421 | 0.010392 | 0.010392 | 0.010382 | 0.010382 | 0.010304 | 0.010421
2015-11-07 | 0.010421 | 0.010421 | 0.017233 | 0.012404 | 0.010372 | 0.010431 | 0.017233
2015-11-08 | 0.010431 | 0.01052 | 0.01052 | 0.01052 | 0.010382 | 0.010382 | 0.01052
2015-11-09 | 0.010206 | 0.010245 | 0.010245 | 0.010294 | 0.010294 | 0.010294 | 0.010294
2015-11-10 | 0.010225 | 0.010284 | 0.010284 | 0.010343 | 0.010343 | 0.010372 | 0.010372
2015-11-11 | 0.010372 | 0.010372 | 0.010343 | 0.010382 | 0.010382 | 0.010431 | 0.010431
2015-11-12 | 0.010431 | 0.01048 | 0.01048 | 0.01048 | 0.010304 | 0.010402 | 0.01048
2015-11-13 | 0.010402 | 0.0105 | 0.0105 | 0.0105 | 0.01049 | 0.0105 | 0.0105
2015-11-14 | 0.0105 | 0.01052 | 0.01052 | 0.01052 | 0.01052 | 0.01052 | 0.01052
2015-11-15 | 0.010441 | 0.010598 | 0.010598 | 0.010677 | 0.010677 | 0.010677 | 0.010677
2015-11-16 | 0.010677 | 0.010755 | 0.010755 | 0.010755 | 0.010628 | 0.010677 | 0.010755
2015-11-17 | 0.010677 | 0.010735 | 0.010735 | 0.010922 | 0.010922 | 0.010922 | 0.010922
2015-11-18 | 0.010735 | 0.010735 | 0.010735 | 0.010804 | 0.010804 | 0.010804 | 0.010804
2015-11-19 | 0.010745 | 0.010902 | 0.011894 | 0.011894 | 0.011894 | 0.011354 | 0.011894
2015-11-20 | 0.011354 | 0.018214 | 0.012502 | 0.046951 | 0.010922 | 0.010922 | 0.046951
2015-11-21 | 0.01103 | 0.013012 | 0.011452 | 0.019451 | 0.011472 | 0.011472 | 0.019451
2015-11-22 | 0.011089 | 0.011197 | 0.013052 | 0.011138 | 0.011138 | 0.010932 | 0.013052
2015-11-23 | 0.011099 | 0.011099 | 0.011256 | 0.011256 | 0.011256 | 0.011108 | 0.011256
2015-11-24 | 0.011118 | 0.01052 | 0.011118 | 0.092334 | 0.01105 | 0.013837 | 0.092334
2015-11-25 | 0.015819 | 0.011 | 0.010824 | 0.011167 | 0.013562 | 0.014975 | 0.015819
2015-11-26 | 0.010853 | 0.019196 | 0.010706 | 0.011933 | 0.011285 | 0.010765 | 0.019196
2015-11-27 | 0.017439 | 0.010716 | 0.011099 | 0.011099 | 0.012836 | 0.012973 | 0.017439
2015-11-28 | 0.012306 | 0.014946 | 0.011913 | 0.010922 | 0.010932 | 0.012041 | 0.014946
2015-11-29 | 0.010981 | 0.010843 | 0.010912 | 0.010912 | 0.010912 | 0.014288 | 0.014288
2015-11-30 | 0.010843 | 0.010912 | 0.010912 | 0.010912 | 0.014288 | 0.012159 | 0.014288
[6 empty] | Max Reading | 0.092334
DATE OF LAST CALIBRATION OF CFE TURBIDIMETER: |  |  |  | ______________

## Unit(1) DI Testing
DATA SHEET FOR INDIVIDUAL MEMBRANE UNIT
DAILY DIRECT INTEGRITY (DI) TESTS AND REPAIRS
(FILL OUT ONE PAGE PER UNIT/SKID)
MONTH | 11 |  |  | PWSID # | 22011
YEAR | 2015 |  |  | PWS NAME | Quinn's Water Treatment Plant
MEMBRANE UNIT # |  |  | 1
Date | Daily DI Test Successful (Indicate Y/N Within Control Limit?) | Describe Results of Triggered** or Unsuccessful DI Tests and any Corrective Actions Taken (Diagnostic tests, module repairs or replacements). Identify serial # of module
** Two 15-min consecutive filtrate turbidity readings exceeding 0.15 NTU triggers DI test – based on turbidity when water is being produced for consumption
2015-11-01 | Y
2015-11-02 | Y
2015-11-03 | Y
2015-11-04 | Y
2015-11-05 | Y
2015-11-06 | Y
2015-11-07 | Y
2015-11-08 | Y
2015-11-09 | Y
2015-11-10 | Y
2015-11-11 | Y
2015-11-12 | Y
2015-11-13 | Y
2015-11-14 | Y
2015-11-15 | Y
2015-11-16 | Y
2015-11-17 | Y
2015-11-18 | Y
2015-11-19 | Y
2015-11-20 | Y
2015-11-21 | Y
2015-11-22 | Y
2015-11-23 | Y
2015-11-24 | Y
2015-11-25 | Y
2015-11-26 | Y
2015-11-27 | Y
2015-11-28 | Y
2015-11-29 | Y
2015-11-30 | Y
If Plant Not Operating Indicate “PO”
Date of Last Chemical Cleaning (CIP) of the Membrane Unit |  |  |  |  | ________________________
Was DI Test Acceptable After Cleaning? |  |  |  |  | ________________________
Date of last Calibration of Individual Unit Filtrate Turbidimeter(s) |  |  |  |  | ________________________

## Unit(2) DI Testing
DATA SHEET FOR INDIVIDUAL MEMBRANE UNIT
DAILY DIRECT INTEGRITY (DI) TESTS AND REPAIRS
(FILL OUT ONE PAGE PER UNIT/SKID)
MONTH | 11 |  |  | PWSID # | 22011
YEAR | 2015 |  |  | PWS NAME | Quinn's Water Treatment Plant
MEMBRANE UNIT # |  |  | 2
Date | Daily DI Test Successful (Indicate Y/N Within Control Limit?) | Describe Results of Triggered** or Unsuccessful DI Tests and any Corrective Actions Taken (Diagnostic tests, module repairs or replacements). Identify serial # of module
** Two 15-min consecutive filtrate turbidity readings exceeding 0.15 NTU triggers DI test – based on turbidity when water is being produced for consumption
2015-11-01 | Y
2015-11-02 | Y
2015-11-03 | Y
2015-11-04 | Y
2015-11-05 | Y
2015-11-06 | Y
2015-11-07 | Y
2015-11-08 | Y
2015-11-09 | Y
2015-11-10 | Y
2015-11-11 | Y
2015-11-12 | Y
2015-11-13 | Y
2015-11-14 | Y
2015-11-15 | Y
2015-11-16 | Y
2015-11-17 | Y
2015-11-18 | Y
2015-11-19 | Y
2015-11-20 | Y
2015-11-21 | Y
2015-11-22 | Y
2015-11-23 | Y
2015-11-24 | Y
2015-11-25 | Y
2015-11-26 | Y
2015-11-27 | Y
2015-11-28 | Y
2015-11-29 | Y
2015-11-30 | Y
If Plant Not Operating Indicate “PO”
Date of Last Chemical Cleaning (CIP) of the Membrane Unit |  |  |  |  | ________________________
Was DI Test Acceptable After Cleaning? |  |  |  |  | ________________________
Date of last Calibration of Individual Unit Filtrate Turbidimeter(s) |  |  |  |  | ________________________

## Unit(3) DI Testing
DATA SHEET FOR INDIVIDUAL MEMBRANE UNIT
DAILY DIRECT INTEGRITY (DI) TESTS AND REPAIRS
(FILL OUT ONE PAGE PER UNIT/SKID)
MONTH | 11 |  |  | PWSID # | 22011
YEAR | 2015 |  |  | PWS NAME | Quinn's Water Treatment Plant
MEMBRANE UNIT # |  |  | 3
Date | Daily DI Test Successful (Indicate Y/N Within Control Limit?) | Describe Results of Triggered** or Unsuccessful DI Tests and any Corrective Actions Taken (Diagnostic tests, module repairs or replacements). Identify serial # of module
** Two 15-min consecutive filtrate turbidity readings exceeding 0.15 NTU triggers DI test – based on turbidity when water is being produced for consumption
2015-11-01 | Y
2015-11-02 | Y
2015-11-03 | Y
2015-11-04 | Y
2015-11-05 | Y
2015-11-06 | Y
2015-11-07 | Y
2015-11-08 | Y
2015-11-09 | Y
2015-11-10 | Y
2015-11-11 | Y
2015-11-12 | Y
2015-11-13 | Y
2015-11-14 | Y
2015-11-15 | Y
2015-11-16 | Y
2015-11-17 | Y
2015-11-18 | Y
2015-11-19 | Y
2015-11-20 | Y
2015-11-21 | Y
2015-11-22 | Y
2015-11-23 | Y
2015-11-24 | Y
2015-11-25 | Y
2015-11-26 | Y
2015-11-27 | Y
2015-11-28 | Y
2015-11-29 | Y
2015-11-30 | Y
If Plant Not Operating Indicate “PO”
Date of Last Chemical Cleaning (CIP) of the Membrane Unit |  |  |  |  | ________________________
Was DI Test Acceptable After Cleaning? |  |  |  |  | ________________________
Date of last Calibration of Individual Unit Filtrate Turbidimeter(s) |  |  |  |  | ________________________

## Unit(4) DI Testing
DATA SHEET FOR INDIVIDUAL MEMBRANE UNIT
DAILY DIRECT INTEGRITY (DI) TESTS AND REPAIRS
(FILL OUT ONE PAGE PER UNIT/SKID)
MONTH | 11 |  |  | PWSID # | 22011
YEAR | 2015 |  |  | PWS NAME | Quinn's Water Treatment Plant
MEMBRANE UNIT # |  |  | 4
Date | Daily DI Test Successful (Indicate Y/N Within Control Limit?) | Describe Results of Triggered** or Unsuccessful DI Tests and any Corrective Actions Taken (Diagnostic tests, module repairs or replacements). Identify serial # of module
** Two 15-min consecutive filtrate turbidity readings exceeding 0.15 NTU triggers DI test – based on turbidity when water is being produced for consumption
2015-11-01 | Y
2015-11-02 | Y
2015-11-03 | Y
2015-11-04 | Y
2015-11-05 | Y
2015-11-06 | Y
2015-11-07 | Y
2015-11-08 | Y
2015-11-09 | Y
2015-11-10 | Y
2015-11-11 | Y
2015-11-12 | Y
2015-11-13 | Y
2015-11-14 | Y
2015-11-15 | Y
2015-11-16 | Y
2015-11-17 | Y
2015-11-18 | Y
2015-11-19 | Y
2015-11-20 | Y
2015-11-21 | Y
2015-11-22 | Y
2015-11-23 | Y
2015-11-24 | Y
2015-11-25 | Y
2015-11-26 | Y
2015-11-27 | Y
2015-11-28 | Y
2015-11-29 | Y
2015-11-30 | Y
If Plant Not Operating Indicate “PO”
Date of Last Chemical Cleaning (CIP) of the Membrane Unit |  |  |  |  | ________________________
Was DI Test Acceptable After Cleaning? |  |  |  |  | ________________________
Date of last Calibration of Individual Unit Filtrate Turbidimeter(s) |  |  |  |  | ________________________

## Operational Worksheet
4-HR VIRUS INACTIVATION CT WORKSHEET FOR INPUT TO MONTHLY REPORTING
Quinns Junction WTP
UPDATED FORMAT, JUNE 7, 2012, Adomonoske
|  |  | Plant Operating Data |  |  |  | CT Calcs | [5 empty] | RESULTS
Min Ratio for Day | Date and Time | Day | Current High Service flow | Temp. | Clearwell Level | Chlorine Residual from the analyzer | Required CTr | Sequence 1 Inlet Pipe Effective Time | Sequence 2 Clearwell Effective Time | Sequence 1 Inlet Pipe CTa | Sequence 2 Clearwell CTa | Total CTa | Compliance Ratio | Status
|  |  | (gpm) | (Deg. F) | (ft) | (mM/L) | (mg-min/L) | (min) | (min) | (mg-min/L) | (mg-min/L) | (mg-min/L) | CTa/CTr
| 2015-11-01 | 1 | 1063.2816 | 48.4759 | 12.603 | 2.2972 | 5.6 | 1.533 | 28.447 | 3.5215 | 65.3474 | 68.8689 | 12.298 | OK
| 2015-11-01 01:00 | 1 | 1078.6467 | 48.4961 | 12.5814 | 2.2972 | 5.6 | 1.5112 | 27.9938 | 3.4714 | 64.3064 | 67.7778 | 12.1032 | OK
1 | 2015-11-01 02:00 | 1 | 3022.7257 | 48.3765 | 34.812 | 2.1462 | 5.6 | 0.53925 | 27.6402 | 1.1573 | 59.3207 | 60.478 | 10.7996 | OK
| 2015-11-01 03:00 | 1 | 1059.5642 | 48.2877 | 12.5825 | 2.1462 | 5.6 | 1.5384 | 28.5004 | 3.3016 | 61.1667 | 64.4683 | 11.5122 | OK
| 2015-11-01 04:00 | 1 | 1058.0105 | 48.2877 | 12.5865 | 2.1462 | 5.6 | 1.5406 | 28.5514 | 3.3065 | 61.2762 | 64.5826 | 11.5326 | OK
| 2015-11-01 05:00 | 1 | 1059.401 | 48.3988 | 12.6051 | 2.1462 | 5.6 | 1.5386 | 28.556 | 3.3021 | 61.2861 | 64.5882 | 11.5336 | OK
| 2015-11-01 06:00 | 1 | 1064.153 | 49.2028 | 12.6015 | 2.1462 | 5.6 | 1.5317 | 28.4204 | 3.2874 | 60.9951 | 64.2825 | 11.479 | OK
| 2015-11-01 07:00 | 1 | 785.885 | 49.2028 | 12.6214 | 2.366 | 5.6 | 2.0741 | 38.5442 | 4.9073 | 91.1947 | 96.102 | 17.1611 | OK
| 2015-11-01 08:00 | 1 | 1059.7635 | 49.2028 | 12.5953 | 2.4211 | 5.6 | 1.5381 | 28.5239 | 3.7238 | 69.0589 | 72.7827 | 12.9969 | OK
| 2015-11-01 09:00 | 1 | 1059.8521 | 49.2028 | 12.596 | 2.4211 | 5.6 | 1.538 | 28.5233 | 3.7235 | 69.0575 | 72.781 | 12.9966 | OK
| 2015-11-01 10:00 | 1 | 1062.7654 | 48.8506 | 12.6025 | 2.4211 | 5.6 | 1.5337 | 28.4598 | 3.7133 | 68.9036 | 72.6169 | 12.9673 | OK
| 2015-11-01 11:00 | 1 | 1059.7266 | 47.5492 | 12.5862 | 2.4211 | 5.95 | 1.5381 | 28.5044 | 3.724 | 69.0116 | 72.7355 | 12.2245 | OK
| 2015-11-01 12:00 | 1 | 1065.8178 | 48.5105 | 12.5751 | 2.4211 | 5.6 | 1.5293 | 28.3166 | 3.7027 | 68.5569 | 72.2596 | 12.9035 | OK
| 2015-11-01 13:00 | 1 | 1064.2509 | 48.7046 | 12.5886 | 2.4211 | 5.6 | 1.5316 | 28.3885 | 3.7081 | 68.7312 | 72.4393 | 12.9356 | OK
| 2015-11-01 14:00 | 1 | 1068.4963 | 48.7046 | 12.6018 | 2.3041 | 5.6 | 1.5255 | 28.3056 | 3.515 | 65.2195 | 68.7345 | 12.274 | OK
| 2015-11-01 15:00 | 1 | 1062.9381 | 48.7046 | 12.6002 | 2.3041 | 5.6 | 1.5335 | 28.4498 | 3.5333 | 65.5519 | 69.0852 | 12.3366 | OK
| 2015-11-01 16:00 | 1 | 1009.3914 | 49.2186 | 12.618 | 2.3041 | 5.6 | 1.6148 | 30.0015 | 3.7208 | 69.1271 | 72.8478 | 13.0085 | OK
| 2015-11-01 17:00 | 1 | 847.2322 | 50.1038 | 12.5831 | 2.2286 | 5.25 | 1.9239 | 35.6447 | 4.2876 | 79.4368 | 83.7244 | 15.9475 | OK
| 2015-11-01 18:00 | 1 | 866.2371 | 50.1038 | 12.5942 | 2.2286 | 5.25 | 1.8817 | 34.8935 | 4.1935 | 77.7627 | 81.9562 | 15.6107 | OK
| 2015-11-01 19:00 | 1 | 860.9275 | 50.1038 | 12.588 | 2.2286 | 5.25 | 1.8933 | 35.0913 | 4.2194 | 78.2035 | 82.4229 | 15.6996 | OK
| 2015-11-01 20:00 | 1 | 862.134 | 50.1038 | 12.59 | 2.2286 | 5.25 | 1.8907 | 35.048 | 4.2135 | 78.1069 | 82.3204 | 15.6801 | OK
| 2015-11-01 21:00 | 1 | 860.9971 | 50.1038 | 12.5877 | 2.2286 | 5.25 | 1.8932 | 35.0878 | 4.219 | 78.1956 | 82.4147 | 15.698 | OK
| 2015-11-01 22:00 | 1 | 859.7857 | 50.1038 | 12.5894 | 2.2286 | 5.25 | 1.8958 | 35.1421 | 4.225 | 78.3166 | 82.5416 | 15.7222 | OK
| 2015-11-01 23:00 | 1 | 859.2529 | 50.1038 | 12.5889 | 2.3178 | 5.25 | 1.897 | 35.1624 | 4.3969 | 81.5001 | 85.897 | 16.3613 | OK
| 2015-11-02 | 2 | 863.1269 | 49.0205 | 12.5858 | 2.3178 | 5.6 | 1.8885 | 34.9961 | 4.3772 | 81.1146 | 85.4917 | 15.2664 | OK
| 2015-11-02 01:00 | 2 | 858.2189 | 47.7541 | 12.5945 | 2.3178 | 5.95 | 1.8993 | 35.2204 | 4.4022 | 81.6346 | 86.0368 | 14.46 | OK
| 2015-11-02 02:00 | 2 | 865.6003 | 47.7541 | 12.5877 | 2.3178 | 5.95 | 1.8831 | 34.9013 | 4.3647 | 80.895 | 85.2597 | 14.3294 | OK
| 2015-11-02 03:00 | 2 | 867.2108 | 47.7541 | 12.598 | 2.3178 | 5.95 | 1.8796 | 34.8647 | 4.3566 | 80.8102 | 85.1668 | 14.3137 | OK
| 2015-11-02 04:00 | 2 | 871.7197 | 47.7541 | 12.5935 | 2.3178 | 5.95 | 1.8699 | 34.6723 | 4.334 | 80.3641 | 84.6981 | 14.235 | OK
| 2015-11-02 05:00 | 2 | 869.1313 | 47.7541 | 12.5884 | 2.1463 | 5.95 | 1.8754 | 34.7614 | 4.0252 | 74.6077 | 78.6329 | 13.2156 | OK
| 2015-11-02 06:00 | 2 | 716.4885 | 47.7541 | 12.5735 | 2.3659 | 5.95 | 2.275 | 42.117 | 5.3823 | 99.6434 | 105.0257 | 17.6514 | OK
| 2015-11-02 07:00 | 2 | 590.387 | 47.7541 | 12.5845 | 2.3659 | 5.95 | 2.7609 | 51.1576 | 6.5319 | 121.0323 | 127.5642 | 21.4394 | OK
| 2015-11-02 08:00 | 2 | 792.2524 | 47.7521 | 13.1214 | 2.3659 | 5.95 | 2.0574 | 39.749 | 4.8676 | 94.041 | 98.9086 | 16.6233 | OK
| 2015-11-02 09:00 | 2 | 1083.4742 | 47.7506 | 12.6194 | 2.3659 | 5.95 | 1.5044 | 27.9532 | 3.5593 | 66.1336 | 69.6928 | 11.7131 | OK
| 2015-11-02 10:00 | 2 | 1061.1646 | 47.7506 | 12.6002 | 2.4004 | 5.95 | 1.536 | 28.4975 | 3.6872 | 68.4064 | 72.0936 | 12.1166 | OK
| 2015-11-02 11:00 | 2 | 1063.2978 | 47.7506 | 12.5858 | 2.4004 | 5.95 | 1.533 | 28.4077 | 3.6798 | 68.1909 | 71.8707 | 12.0791 | OK
| 2015-11-02 12:00 | 2 | 1063.2505 | 47.767 | 12.5904 | 2.1326 | 5.95 | 1.533 | 28.4193 | 3.2693 | 60.6065 | 63.8758 | 10.7354 | OK
| 2015-11-02 13:00 | 2 | 1059.9861 | 47.7965 | 12.5932 | 2.1326 | 5.95 | 1.5378 | 28.5133 | 3.2794 | 60.807 | 64.0864 | 10.7708 | OK
| 2015-11-02 14:00 | 2 | 1064.2249 | 47.7965 | 12.5832 | 2.1326 | 5.95 | 1.5316 | 28.3772 | 3.2663 | 60.5167 | 63.783 | 10.7198 | OK
| 2015-11-02 15:00 | 2 | 1064.2563 | 47.7965 | 12.5906 | 2.1326 | 5.95 | 1.5316 | 28.3931 | 3.2662 | 60.5506 | 63.8168 | 10.7255 | OK
1 | 2015-11-02 16:00 | 2 | 1409.2079 | 49.0646 | 12.6021 | 1.9745 | 5.6 | 1.1567 | 21.4625 | 2.2839 | 42.3782 | 44.6621 | 7.9754 | OK
| 2015-11-02 17:00 | 2 | 1428.8736 | 49.3264 | 12.5863 | 2.3385 | 5.6 | 1.1408 | 21.1405 | 2.6676 | 49.4365 | 52.1041 | 9.3043 | OK
| 2015-11-02 18:00 | 2 | 1443.4076 | 48.9063 | 12.6035 | 2.3385 | 5.6 | 1.1293 | 20.9562 | 2.6408 | 49.0056 | 51.6464 | 9.2226 | OK
| 2015-11-02 19:00 | 2 | 1076.3224 | 48.8616 | 12.5996 | 2.3385 | 5.6 | 1.5144 | 28.0948 | 3.5414 | 65.6991 | 69.2405 | 12.3644 | OK
| 2015-11-02 20:00 | 2 | 1063.2235 | 47.4503 | 12.6009 | 2.3385 | 5.95 | 1.5331 | 28.4439 | 3.5851 | 66.5154 | 70.1005 | 11.7816 | OK
| 2015-11-02 21:00 | 2 | 1060.1176 | 47.4503 | 12.5951 | 2.3385 | 5.95 | 1.5376 | 28.5139 | 3.5956 | 66.6791 | 70.2747 | 11.8109 | OK
| 2015-11-02 22:00 | 2 | 1061.9628 | 47.4503 | 12.6021 | 2.3385 | 5.95 | 1.5349 | 28.4803 | 3.5893 | 66.6004 | 70.1897 | 11.7966 | OK
| 2015-11-02 23:00 | 2 | 1066.0115 | 47.4503 | 12.6047 | 2.3385 | 5.95 | 1.5291 | 28.378 | 3.5757 | 66.3611 | 69.9368 | 11.7541 | OK
| 2015-11-03 | 3 | 1064.8934 | 47.4503 | 12.5946 | 2.3385 | 5.95 | 1.5307 | 28.385 | 3.5794 | 66.3776 | 69.957 | 11.7575 | OK
| 2015-11-03 01:00 | 3 | 1063.159 | 47.4503 | 12.5902 | 2.3179 | 5.95 | 1.5332 | 28.4214 | 3.5538 | 65.8787 | 69.4324 | 11.6693 | OK
| 2015-11-03 02:00 | 3 | 1068.1976 | 47.4503 | 12.5971 | 2.2835 | 5.95 | 1.5259 | 28.3029 | 3.4844 | 64.6287 | 68.1132 | 11.4476 | OK
1 | 2015-11-03 03:00 | 3 | 1069.667 | 47.4477 | 12.6068 | 2.2835 | 5.95 | 1.5238 | 28.2856 | 3.4796 | 64.5894 | 68.069 | 11.4402 | OK
| 2015-11-03 04:00 | 3 | 1064.4669 | 47.4044 | 12.5967 | 2.2835 | 5.95 | 1.5313 | 28.4012 | 3.4966 | 64.8532 | 68.3499 | 11.4874 | OK
| 2015-11-03 05:00 | 3 | 1067.8239 | 47.4044 | 12.5861 | 2.2835 | 5.95 | 1.5265 | 28.2881 | 3.4856 | 64.5949 | 68.0806 | 11.4421 | OK
| 2015-11-03 06:00 | 3 | 1061.7674 | 47.4044 | 12.5993 | 2.2835 | 5.95 | 1.5352 | 28.4792 | 3.5055 | 65.0314 | 68.5369 | 11.5188 | OK
| 2015-11-03 07:00 | 3 | 1058.2443 | 47.4044 | 12.5803 | 2.2835 | 5.95 | 1.5403 | 28.531 | 3.5172 | 65.1497 | 68.6669 | 11.5407 | OK
| 2015-11-03 08:00 | 3 | 658.9495 | 47.4044 | 12.5926 | 2.2835 | 5.95 | 2.4736 | 45.8643 | 5.6485 | 104.7297 | 110.3782 | 18.551 | OK
| 2015-11-03 09:00 | 3 | 672.305 | 47.4044 | 12.5734 | 2.3797 | 5.95 | 2.4245 | 44.8846 | 5.7695 | 106.8107 | 112.5802 | 18.921 | OK
| 2015-11-03 10:00 | 3 | 853.093 | 47.4044 | 12.5871 | 2.3797 | 5.95 | 1.9107 | 35.4113 | 4.5468 | 84.2673 | 88.8141 | 14.9267 | OK
| 2015-11-03 11:00 | 3 | 872.0992 | 47.3972 | 12.5989 | 2.0158 | 5.95 | 1.8691 | 34.6718 | 3.7677 | 69.8924 | 73.6601 | 12.3799 | OK
| 2015-11-03 12:00 | 3 | 873.6718 | 47.3019 | 12.5984 | 2.0157 | 5.95 | 1.8657 | 34.6083 | 3.7607 | 69.7606 | 73.5214 | 12.3565 | OK
| 2015-11-03 13:00 | 3 | 869.4804 | 47.3019 | 12.5906 | 2.0157 | 5.95 | 1.8747 | 34.7535 | 3.7788 | 70.0534 | 73.8322 | 12.4088 | OK
| 2015-11-03 14:00 | 3 | 872.4535 | 47.3019 | 12.5853 | 2.0157 | 5.95 | 1.8683 | 34.6205 | 3.766 | 69.7854 | 73.5514 | 12.3616 | OK
| 2015-11-03 15:00 | 3 | 840.7185 | 47.3922 | 12.581 | 2.0157 | 5.95 | 1.9388 | 35.9149 | 3.9081 | 72.3945 | 76.3026 | 12.824 | OK
| 2015-11-03 16:00 | 3 | 868.7655 | 49.0402 | 12.5971 | 2.3178 | 5.6 | 1.8762 | 34.7999 | 4.3488 | 80.66 | 85.0087 | 15.1801 | OK
| 2015-11-03 17:00 | 3 | 874.1471 | 49.0402 | 12.5932 | 2.3178 | 5.6 | 1.8647 | 34.575 | 4.322 | 80.1387 | 84.4606 | 15.0823 | OK
| 2015-11-03 18:00 | 3 | 874.1533 | 49.0402 | 12.5912 | 2.3384 | 5.6 | 1.8647 | 34.5693 | 4.3603 | 80.8358 | 85.196 | 15.2136 | OK
| 2015-11-03 19:00 | 3 | 868.5869 | 49.0402 | 12.5867 | 2.3728 | 5.6 | 1.8766 | 34.7783 | 4.4529 | 82.5229 | 86.9758 | 15.5314 | OK
| 2015-11-03 20:00 | 3 | 868.733 | 49.0402 | 12.5991 | 2.4415 | 5.6 | 1.8763 | 34.8069 | 4.581 | 84.9819 | 89.563 | 15.9934 | OK
| 2015-11-03 21:00 | 3 | 854.7138 | 49.0402 | 12.5833 | 2.3385 | 5.6 | 1.9071 | 35.3334 | 4.4596 | 82.6263 | 87.086 | 15.5511 | OK
| 2015-11-03 22:00 | 3 | 850.7371 | 48.8245 | 12.5904 | 2.3385 | 5.6 | 1.916 | 35.5185 | 4.4805 | 83.0591 | 87.5396 | 15.6321 | OK
| 2015-11-03 23:00 | 3 | 850.9928 | 48.0085 | 12.5802 | 2.1255 | 5.95 | 1.9154 | 35.4791 | 4.0712 | 75.4115 | 79.4828 | 13.3584 | OK
| 2015-11-04 | 4 | 867.7879 | 48.0085 | 12.5965 | 2.1255 | 5.95 | 1.8783 | 34.8375 | 3.9924 | 74.0478 | 78.0402 | 13.116 | OK
| 2015-11-04 01:00 | 4 | 866.363 | 48.0085 | 12.5951 | 2.1255 | 5.95 | 1.8814 | 34.891 | 3.999 | 74.1615 | 78.1605 | 13.1362 | OK
| 2015-11-04 02:00 | 4 | 871.6405 | 48.0085 | 12.5993 | 2.1255 | 5.95 | 1.87 | 34.6913 | 3.9748 | 73.7371 | 77.7119 | 13.0608 | OK
| 2015-11-04 03:00 | 4 | 882.8439 | 48.0085 | 12.5962 | 2.1255 | 5.95 | 1.8463 | 34.2427 | 3.9244 | 72.7835 | 76.7078 | 12.8921 | OK
| 2015-11-04 04:00 | 4 | 869.2118 | 48.0085 | 12.5946 | 2.1255 | 5.95 | 1.8753 | 34.7752 | 3.9859 | 73.9152 | 77.9011 | 13.0926 | OK
| 2015-11-04 05:00 | 4 | 874.4893 | 48.0085 | 12.6011 | 2.1255 | 5.95 | 1.8639 | 34.5832 | 3.9618 | 73.5071 | 77.469 | 13.02 | OK
| 2015-11-04 06:00 | 4 | 865.8675 | 47.8377 | 12.5892 | 2.1255 | 5.95 | 1.8825 | 34.8946 | 4.0013 | 74.1692 | 78.1705 | 13.1379 | OK
| 2015-11-04 07:00 | 4 | 871.1399 | 47.3302 | 12.5924 | 2.3385 | 5.95 | 1.8711 | 34.6922 | 4.3755 | 81.1269 | 85.5025 | 14.3702 | OK
| 2015-11-04 08:00 | 4 | 871.7219 | 47.3302 | 12.6017 | 2.3385 | 5.95 | 1.8699 | 34.6947 | 4.3726 | 81.1325 | 85.5052 | 14.3706 | OK
| 2015-11-04 09:00 | 4 | 869.1095 | 47.3302 | 12.5925 | 2.3385 | 5.95 | 1.8755 | 34.7735 | 4.3858 | 81.3169 | 85.7027 | 14.4038 | OK
| 2015-11-04 10:00 | 4 | 869.5491 | 47.3302 | 12.5994 | 2.3385 | 5.95 | 1.8745 | 34.7749 | 4.3836 | 81.3202 | 85.7037 | 14.404 | OK
| 2015-11-04 11:00 | 4 | 401.878 | 47.3302 | 12.7066 | 2.3385 | 5.95 | 4.056 | 75.8835 | 9.4848 | 177.4515 | 186.9363 | 31.4179 | OK
| 2015-11-04 12:00 | 4 | 0 | 47.3302 | 12.8806 | 2.2836 | 5.95 | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | PO | OK
| 2015-11-04 13:00 | 4 | 765.3267 | 47.3302 | 12.6346 | 2.1668 | 5.95 | 2.1298 | 39.6211 | 4.6149 | 85.852 | 90.4669 | 15.2045 | OK
| 2015-11-04 14:00 | 4 | 874.6647 | 47.0088 | 12.5945 | 2.1668 | 5.95 | 1.8636 | 34.5581 | 4.038 | 74.8814 | 78.9195 | 13.2638 | OK
| 2015-11-04 15:00 | 4 | 864.7901 | 46.8072 | 12.5947 | 2.1668 | 5.95 | 1.8849 | 34.9533 | 4.0841 | 75.7376 | 79.8217 | 13.4154 | OK
| 2015-11-04 16:00 | 4 | 867.741 | 46.8072 | 12.5884 | 2.3591 | 5.95 | 1.8784 | 34.817 | 4.4315 | 82.1378 | 86.5692 | 14.5495 | OK
| 2015-11-04 17:00 | 4 | 862.9514 | 48.2198 | 12.5883 | 2.3591 | 5.6 | 1.8889 | 35.0099 | 4.4561 | 82.5929 | 87.049 | 15.5445 | OK
| 2015-11-04 18:00 | 4 | 918.0842 | 48.4325 | 12.5974 | 2.3591 | 5.6 | 1.7754 | 32.9313 | 4.1885 | 77.6892 | 81.8777 | 14.621 | OK
| 2015-11-04 19:00 | 4 | 1062.2348 | 48.4325 | 12.6036 | 2.3591 | 5.6 | 1.5345 | 28.4765 | 3.6201 | 67.1798 | 70.7999 | 12.6428 | OK
| 2015-11-04 20:00 | 4 | 1066.582 | 48.4325 | 12.6003 | 2.3453 | 5.6 | 1.5282 | 28.3529 | 3.5842 | 66.4968 | 70.081 | 12.5145 | OK
| 2015-11-04 21:00 | 4 | 1062.8277 | 48.4325 | 12.6047 | 2.3453 | 5.6 | 1.5336 | 28.463 | 3.5969 | 66.755 | 70.3519 | 12.5628 | OK
| 2015-11-04 22:00 | 4 | 1064.9467 | 46.7093 | 12.5945 | 2.3453 | 5.95 | 1.5306 | 28.3834 | 3.5897 | 66.5684 | 70.1581 | 11.7913 | OK
1 | 2015-11-04 23:00 | 4 | 1065.7365 | 46.1925 | 12.6004 | 2.3453 | 6.3 | 1.5295 | 28.3756 | 3.5871 | 66.5501 | 70.1371 | 11.1329 | OK
| 2015-11-05 | 5 | 1063.1944 | 46.1925 | 12.6045 | 2.3453 | 6.3 | 1.5331 | 28.4527 | 3.5957 | 66.7309 | 70.3265 | 11.1629 | OK
| 2015-11-05 01:00 | 5 | 1073.9103 | 46.1925 | 12.5912 | 2.3453 | 6.3 | 1.5178 | 28.1391 | 3.5598 | 65.9952 | 69.555 | 11.0405 | OK
| 2015-11-05 02:00 | 5 | 1073.6333 | 46.1925 | 12.5999 | 2.3453 | 6.3 | 1.5182 | 28.1658 | 3.5607 | 66.0579 | 69.6186 | 11.0506 | OK
| 2015-11-05 03:00 | 5 | 1073.5363 | 46.1925 | 12.6037 | 2.3453 | 6.3 | 1.5183 | 28.1768 | 3.561 | 66.0838 | 69.6448 | 11.0547 | OK
| 2015-11-05 04:00 | 5 | 1070.2633 | 46.1925 | 12.5989 | 2.3247 | 6.3 | 1.523 | 28.2522 | 3.5404 | 65.677 | 69.2174 | 10.9869 | OK
| 2015-11-05 05:00 | 5 | 1075.638 | 46.1925 | 12.6053 | 2.2493 | 6.3 | 1.5154 | 28.1253 | 3.4086 | 63.2631 | 66.6717 | 10.5828 | OK
| 2015-11-05 06:00 | 5 | 1067.3114 | 45.8776 | 12.6022 | 2.2493 | 6.3 | 1.5272 | 28.3379 | 3.4352 | 63.7413 | 67.1765 | 10.6629 | OK
| 2015-11-05 07:00 | 5 | 1067.6402 | 45.7967 | 12.6037 | 2.2563 | 6.3 | 1.5267 | 28.3324 | 3.4447 | 63.926 | 67.3708 | 10.6938 | OK
| 2015-11-05 08:00 | 5 | 1072.4367 | 45.7967 | 12.6071 | 2.2563 | 6.3 | 1.5199 | 28.2134 | 3.4293 | 63.6576 | 67.0869 | 10.6487 | OK
| 2015-11-05 09:00 | 5 | 1071.7566 | 45.7967 | 12.6089 | 2.2563 | 6.3 | 1.5209 | 28.2352 | 3.4315 | 63.7069 | 67.1384 | 10.6569 | OK
| 2015-11-05 10:00 | 5 | 1071.1765 | 45.7967 | 12.6084 | 2.2563 | 6.3 | 1.5217 | 28.2495 | 3.4334 | 63.7391 | 67.1725 | 10.6623 | OK
| 2015-11-05 11:00 | 5 | 1076.9744 | 45.7627 | 12.6101 | 2.2563 | 6.3 | 1.5135 | 28.1013 | 3.4149 | 63.4046 | 66.8194 | 10.6063 | OK
| 2015-11-05 12:00 | 5 | 1065.3581 | 45.7473 | 12.6055 | 2.2563 | 6.3 | 1.53 | 28.3972 | 3.4521 | 64.0723 | 67.5245 | 10.7182 | OK
| 2015-11-05 13:00 | 5 | 1071.3448 | 45.7907 | 12.6146 | 2.2563 | 6.3 | 1.5215 | 28.2589 | 3.4328 | 63.7603 | 67.1931 | 10.6656 | OK
| 2015-11-05 14:00 | 5 | 1068.8647 | 46.0299 | 12.6091 | 2.105 | 6.3 | 1.525 | 28.3121 | 3.21 | 59.5962 | 62.8062 | 9.9692 | OK
| 2015-11-05 15:00 | 5 | 1072.1978 | 46.0299 | 12.6061 | 2.105 | 6.3 | 1.5202 | 28.2175 | 3.2001 | 59.3969 | 62.597 | 9.936 | OK
| 2015-11-05 16:00 | 5 | 1072.6818 | 46.0299 | 12.6094 | 2.105 | 6.3 | 1.5196 | 28.2121 | 3.1986 | 59.3856 | 62.5843 | 9.934 | OK
| 2015-11-05 17:00 | 5 | 1072.0423 | 46.0299 | 12.6089 | 2.105 | 6.3 | 1.5205 | 28.2279 | 3.2005 | 59.4188 | 62.6194 | 9.9396 | OK
1 | 2015-11-05 18:00 | 5 | 1074.7452 | 46.0299 | 12.6052 | 2.105 | 6.3 | 1.5166 | 28.1485 | 3.1925 | 59.2518 | 62.4443 | 9.9118 | OK
| 2015-11-05 19:00 | 5 | 1067.8647 | 46.0299 | 12.6081 | 2.105 | 6.3 | 1.5264 | 28.3364 | 3.2131 | 59.6473 | 62.8603 | 9.9778 | OK
| 2015-11-05 20:00 | 5 | 1070.0455 | 46.0299 | 12.6014 | 2.105 | 6.3 | 1.5233 | 28.2637 | 3.2065 | 59.4943 | 62.7009 | 9.9525 | OK
| 2015-11-05 21:00 | 5 | 1069.9617 | 45.7914 | 12.6045 | 2.105 | 6.3 | 1.5234 | 28.2728 | 3.2068 | 59.5134 | 62.7201 | 9.9556 | OK
| 2015-11-05 22:00 | 5 | 1075.9934 | 44.6025 | 12.6147 | 2.3041 | 6.3 | 1.5149 | 28.1371 | 3.4905 | 64.8313 | 68.3218 | 10.8447 | OK
| 2015-11-05 23:00 | 5 | 1073.4176 | 44.6025 | 12.6007 | 2.3041 | 6.3 | 1.5185 | 28.1733 | 3.4988 | 64.9148 | 68.4137 | 10.8593 | OK
| 2015-11-06 | 6 | 1070.0499 | 44.6025 | 12.6084 | 2.3041 | 6.3 | 1.5233 | 28.2792 | 3.5099 | 65.1587 | 68.6685 | 10.8998 | OK
| 2015-11-06 01:00 | 6 | 1063.9733 | 44.6025 | 12.6139 | 2.3041 | 6.3 | 1.532 | 28.4532 | 3.5299 | 65.5596 | 69.0895 | 10.9666 | OK
| 2015-11-06 02:00 | 6 | 1070.6655 | 44.6025 | 12.6051 | 2.3041 | 6.3 | 1.5224 | 28.2556 | 3.5078 | 65.1043 | 68.6121 | 10.8908 | OK
| 2015-11-06 03:00 | 6 | 1078.5048 | 44.6025 | 12.6121 | 2.3041 | 6.3 | 1.5114 | 28.0657 | 3.4823 | 64.6669 | 68.1492 | 10.8173 | OK
| 2015-11-06 04:00 | 6 | 1077.8461 | 44.6025 | 12.6083 | 2.3041 | 6.3 | 1.5123 | 28.0744 | 3.4845 | 64.6869 | 68.1713 | 10.8208 | OK
| 2015-11-06 05:00 | 6 | 1079.0411 | 44.5122 | 12.6121 | 2.3178 | 6.3 | 1.5106 | 28.0517 | 3.5013 | 65.0189 | 68.5202 | 10.8762 | OK
| 2015-11-06 06:00 | 6 | 1073.9488 | 44.2244 | 12.597 | 2.2698 | 6.3 | 1.5178 | 28.1511 | 3.445 | 63.8967 | 67.3416 | 10.6891 | OK
| 2015-11-06 07:00 | 6 | 1074.1086 | 44.2244 | 12.6082 | 2.2698 | 6.3 | 1.5175 | 28.172 | 3.4445 | 63.944 | 67.3885 | 10.6966 | OK
| 2015-11-06 08:00 | 6 | 1069.1089 | 44.2244 | 12.6107 | 2.2698 | 6.3 | 1.5246 | 28.3093 | 3.4606 | 64.2556 | 67.7162 | 10.7486 | OK
| 2015-11-06 09:00 | 6 | 1062.5029 | 44.2244 | 12.6024 | 2.2698 | 6.3 | 1.5341 | 28.4665 | 3.4821 | 64.6125 | 68.0946 | 10.8087 | OK
| 2015-11-06 10:00 | 6 | 1072.6108 | 44.2244 | 12.6146 | 2.2698 | 6.3 | 1.5197 | 28.2255 | 3.4493 | 64.0655 | 67.5147 | 10.7166 | OK
| 2015-11-06 11:00 | 6 | 1061.7424 | 44.2806 | 12.6066 | 2.2698 | 6.3 | 1.5352 | 28.4963 | 3.4846 | 64.6802 | 68.1648 | 10.8198 | OK
| 2015-11-06 12:00 | 6 | 1379.2024 | 44.2951 | 12.617 | 2.3249 | 6.3 | 1.1818 | 21.9553 | 2.7476 | 51.0436 | 53.7912 | 8.5383 | OK
| 2015-11-06 13:00 | 6 | 1443.8407 | 45.1492 | 12.5985 | 2.3249 | 6.3 | 1.1289 | 20.9417 | 2.6246 | 48.6871 | 51.3117 | 8.1447 | OK
1 | 2015-11-06 14:00 | 6 | 1455.8032 | 45.1961 | 12.6026 | 2.3249 | 6.3 | 1.1197 | 20.7763 | 2.6031 | 48.3024 | 50.9055 | 8.0802 | OK
| 2015-11-06 15:00 | 6 | 1235.5421 | 45.1961 | 12.6233 | 2.3249 | 6.3 | 1.3193 | 24.5203 | 3.0671 | 57.0069 | 60.074 | 9.5356 | OK
| 2015-11-06 16:00 | 6 | 1073.3611 | 45.1961 | 12.6088 | 2.3249 | 6.3 | 1.5186 | 28.1929 | 3.5306 | 65.5452 | 69.0757 | 10.9644 | OK
| 2015-11-06 17:00 | 6 | 1070.4777 | 43.9923 | 12.6087 | 2.3249 | 6.3 | 1.5227 | 28.2685 | 3.5401 | 65.7209 | 69.261 | 10.9938 | OK
| 2015-11-06 18:00 | 6 | 1066.0468 | 43.5284 | 12.6029 | 2.3249 | 6.65 | 1.529 | 28.373 | 3.5548 | 65.9639 | 69.5187 | 10.4539 | OK
| 2015-11-06 19:00 | 6 | 1067.9592 | 43.5284 | 12.6041 | 2.3249 | 6.65 | 1.5263 | 28.3248 | 3.5484 | 65.8519 | 69.4003 | 10.4361 | OK
| 2015-11-06 20:00 | 6 | 1070.1204 | 43.5284 | 12.5958 | 2.311 | 6.65 | 1.5232 | 28.249 | 3.5201 | 65.2827 | 68.8027 | 10.3463 | OK
| 2015-11-06 21:00 | 6 | 1074.9197 | 43.5284 | 12.6069 | 2.311 | 6.65 | 1.5164 | 28.1477 | 3.5043 | 65.0485 | 68.5528 | 10.3087 | OK
| 2015-11-06 22:00 | 6 | 1072.754 | 43.5284 | 12.61 | 2.2563 | 6.65 | 1.5195 | 28.2115 | 3.4283 | 63.6533 | 67.0816 | 10.0875 | OK
| 2015-11-06 23:00 | 6 | 1085.1891 | 43.5284 | 12.6055 | 2.3179 | 6.65 | 1.502 | 27.8782 | 3.4816 | 64.6198 | 68.1014 | 10.2408 | OK
| 2015-11-07 | 7 | 1074.5652 | 43.5284 | 12.6076 | 2.3179 | 6.65 | 1.5169 | 28.1587 | 3.516 | 65.2697 | 68.7858 | 10.3437 | OK
| 2015-11-07 01:00 | 7 | 1078.8166 | 43.3491 | 12.6073 | 2.3179 | 6.65 | 1.5109 | 28.0471 | 3.5022 | 65.011 | 68.5132 | 10.3027 | OK
| 2015-11-07 02:00 | 7 | 1076.3279 | 43.2881 | 12.5954 | 2.3179 | 6.65 | 1.5144 | 28.0852 | 3.5103 | 65.0995 | 68.6098 | 10.3173 | OK
| 2015-11-07 03:00 | 7 | 1080.6994 | 43.2881 | 12.5996 | 2.3179 | 6.65 | 1.5083 | 27.981 | 3.4961 | 64.8579 | 68.354 | 10.2788 | OK
| 2015-11-07 04:00 | 7 | 1074.2735 | 43.2881 | 12.5991 | 2.3179 | 6.65 | 1.5173 | 28.1471 | 3.517 | 65.243 | 68.76 | 10.3399 | OK
| 2015-11-07 05:00 | 7 | 1074.6058 | 43.2881 | 12.609 | 2.3179 | 6.65 | 1.5168 | 28.1606 | 3.5159 | 65.2742 | 68.7901 | 10.3444 | OK
| 2015-11-07 06:00 | 7 | 1072.1515 | 43.2881 | 12.6079 | 2.3179 | 6.65 | 1.5203 | 28.2226 | 3.524 | 65.4179 | 68.9419 | 10.3672 | OK
| 2015-11-07 07:00 | 7 | 1069.9949 | 43.2881 | 12.6002 | 2.3041 | 6.65 | 1.5234 | 28.2623 | 3.51 | 65.1197 | 68.6297 | 10.3203 | OK
| 2015-11-07 08:00 | 7 | 1069.8926 | 43.2881 | 12.6002 | 2.3041 | 6.65 | 1.5235 | 28.265 | 3.5104 | 65.1261 | 68.6364 | 10.3213 | OK
| 2015-11-07 09:00 | 7 | 1080.1199 | 42.8279 | 12.6046 | 2.3041 | 6.65 | 1.5091 | 28.007 | 3.4771 | 64.5316 | 68.0088 | 10.2269 | OK
| 2015-11-07 10:00 | 7 | 1074.9703 | 42.7016 | 12.5981 | 2.3041 | 7 | 1.5163 | 28.1268 | 3.4938 | 64.8077 | 68.3015 | 9.7574 | OK
| 2015-11-07 11:00 | 7 | 1072.7811 | 43.0122 | 12.6067 | 2.3041 | 6.65 | 1.5194 | 28.2033 | 3.5009 | 64.9839 | 68.4848 | 10.2985 | OK
| 2015-11-07 12:00 | 7 | 1071.9887 | 43.0514 | 12.6047 | 2.3041 | 6.65 | 1.5205 | 28.2199 | 3.5035 | 65.0221 | 68.5256 | 10.3046 | OK
| 2015-11-07 13:00 | 7 | 1073.5296 | 43.6647 | 12.6049 | 2.3041 | 6.65 | 1.5184 | 28.1797 | 3.4985 | 64.9295 | 68.4279 | 10.2899 | OK
| 2015-11-07 14:00 | 7 | 1046.6436 | 44.2633 | 12.5951 | 2.3042 | 6.3 | 1.5574 | 28.8811 | 3.5885 | 66.5487 | 70.1372 | 11.1329 | OK
| 2015-11-07 15:00 | 7 | 1115.5243 | 44.2633 | 12.5967 | 2.3042 | 6.3 | 1.4612 | 27.1011 | 3.3669 | 62.4473 | 65.8142 | 10.4467 | OK
| 2015-11-07 16:00 | 7 | 1161.1862 | 44.2633 | 12.6011 | 2.3042 | 6.3 | 1.4037 | 26.0447 | 3.2345 | 60.013 | 63.2475 | 10.0393 | OK
| 2015-11-07 17:00 | 7 | 1160.5693 | 44.2633 | 12.5942 | 2.3455 | 6.3 | 1.4045 | 26.0443 | 3.2943 | 61.0878 | 64.3821 | 10.2194 | OK
| 2015-11-07 18:00 | 7 | 1156.628 | 44.2633 | 12.5931 | 2.3455 | 6.3 | 1.4093 | 26.1306 | 3.3055 | 61.2904 | 64.5959 | 10.2533 | OK
| 2015-11-07 19:00 | 7 | 1162.3214 | 41.0839 | 12.6092 | 2.3455 | 7 | 1.4024 | 26.0359 | 3.2893 | 61.0682 | 64.3575 | 9.1939 | OK
| 2015-11-07 20:00 | 7 | 1161.8875 | 41.0798 | 12.6109 | 2.1324 | 7 | 1.4029 | 26.0491 | 2.9915 | 55.5462 | 58.5377 | 8.3625 | OK
| 2015-11-07 21:00 | 7 | 1227.4098 | 41.0798 | 12.5993 | 2.1324 | 7 | 1.328 | 24.6358 | 2.8318 | 52.5326 | 55.3644 | 7.9092 | OK
| 2015-11-07 22:00 | 7 | 1258.2208 | 41.0798 | 12.6246 | 2.1324 | 7 | 1.2955 | 24.0809 | 2.7624 | 51.3492 | 54.1117 | 7.7302 | OK
1 | 2015-11-07 23:00 | 7 | 1265.2648 | 41.0798 | 12.6048 | 2.1324 | 7 | 1.2883 | 23.9092 | 2.7471 | 50.9831 | 53.7301 | 7.6757 | OK
| 2015-11-08 | 8 | 1266.8241 | 41.0798 | 12.6158 | 2.1324 | 7 | 1.2867 | 23.9006 | 2.7437 | 50.9649 | 53.7086 | 7.6727 | OK
| 2015-11-08 01:00 | 8 | 1263.1623 | 41.0798 | 12.6137 | 2.1324 | 7 | 1.2904 | 23.9659 | 2.7516 | 51.1041 | 53.8557 | 7.6937 | OK
| 2015-11-08 02:00 | 8 | 1256.5981 | 41.0022 | 12.6138 | 2.1324 | 7 | 1.2972 | 24.0913 | 2.766 | 51.3715 | 54.1375 | 7.7339 | OK
1 | 2015-11-08 03:00 | 8 | 1255.233 | 40.5817 | 12.6123 | 2.1324 | 7.7875 | 1.2986 | 24.1147 | 2.769 | 51.4213 | 54.1903 | 6.9586 | OK
| 2015-11-08 04:00 | 8 | 1254.1776 | 40.5817 | 12.6118 | 2.1324 | 7.7875 | 1.2997 | 24.1341 | 2.7713 | 51.4627 | 54.2341 | 6.9642 | OK
| 2015-11-08 05:00 | 8 | 1256.2188 | 40.5817 | 12.6141 | 2.3452 | 7.7875 | 1.2975 | 24.0992 | 3.043 | 56.5179 | 59.5609 | 7.6483 | OK
| 2015-11-08 06:00 | 8 | 1253.1722 | 40.5817 | 12.6028 | 2.3452 | 7.7875 | 1.3007 | 24.1362 | 3.0504 | 56.6047 | 59.6551 | 7.6604 | OK
| 2015-11-08 07:00 | 8 | 1252.9404 | 40.5817 | 12.6136 | 2.3452 | 7.7875 | 1.3009 | 24.1613 | 3.051 | 56.6635 | 59.7145 | 7.668 | OK
| 2015-11-08 08:00 | 8 | 1276.6244 | 42.8906 | 12.616 | 2.3452 | 6.65 | 1.2768 | 23.7175 | 2.9944 | 55.6227 | 58.617 | 8.8146 | OK
| 2015-11-08 09:00 | 8 | 1129.2231 | 43.3588 | 12.5952 | 2.3452 | 6.65 | 1.4435 | 26.7693 | 3.3852 | 62.7798 | 66.1651 | 9.9496 | OK
| 2015-11-08 10:00 | 8 | 1071.3006 | 43.3588 | 12.6052 | 2.3452 | 6.65 | 1.5215 | 28.2391 | 3.5683 | 66.2268 | 69.7951 | 10.4955 | OK
| 2015-11-08 11:00 | 8 | 1062.0786 | 43.3588 | 12.6006 | 2.3452 | 6.65 | 1.5347 | 28.4739 | 3.5993 | 66.7775 | 70.3767 | 10.583 | OK
| 2015-11-08 12:00 | 8 | 1070.9146 | 43.4602 | 12.6037 | 2.318 | 6.65 | 1.5221 | 28.2458 | 3.5282 | 65.4748 | 69.003 | 10.3764 | OK
| 2015-11-08 13:00 | 8 | 1073.024 | 44.0866 | 12.6026 | 2.0639 | 6.3 | 1.5191 | 28.1878 | 3.1352 | 58.1761 | 61.3113 | 9.732 | OK
| 2015-11-08 14:00 | 8 | 1236.7103 | 44.0866 | 12.6027 | 2.0639 | 6.3 | 1.318 | 24.4572 | 2.7202 | 50.4768 | 53.197 | 8.444 | OK
| 2015-11-08 15:00 | 8 | 1248.5073 | 44.0866 | 12.6077 | 2.0639 | 6.3 | 1.3056 | 24.2357 | 2.6945 | 50.0196 | 52.7141 | 8.3673 | OK
| 2015-11-08 16:00 | 8 | 1252.7025 | 44.0866 | 12.6046 | 2.0639 | 6.3 | 1.3012 | 24.1486 | 2.6855 | 49.8398 | 52.5253 | 8.3374 | OK
| 2015-11-08 17:00 | 8 | 1253.772 | 44.0866 | 12.6138 | 2.0639 | 6.3 | 1.3001 | 24.1457 | 2.6832 | 49.8338 | 52.517 | 8.336 | OK
| 2015-11-08 18:00 | 8 | 1253.9842 | 44.0866 | 12.6041 | 2.0639 | 6.3 | 1.2999 | 24.123 | 2.6827 | 49.7869 | 52.4696 | 8.3285 | OK
| 2015-11-08 19:00 | 8 | 1258.5136 | 44.0866 | 12.5992 | 2.0639 | 6.3 | 1.2952 | 24.0268 | 2.6731 | 49.5883 | 52.2614 | 8.2955 | OK
| 2015-11-08 20:00 | 8 | 1258.7025 | 43.5957 | 12.6072 | 2.0639 | 6.65 | 1.295 | 24.0385 | 2.6727 | 49.6125 | 52.2852 | 7.8624 | OK
| 2015-11-08 21:00 | 8 | 1253.97 | 41.5356 | 12.6042 | 2.359 | 7 | 1.2999 | 24.1234 | 3.0664 | 56.9077 | 59.9741 | 8.5677 | OK
| 2015-11-08 22:00 | 8 | 1251.7797 | 41.5356 | 12.5952 | 2.359 | 7 | 1.3021 | 24.1484 | 3.0718 | 56.9667 | 60.0385 | 8.5769 | OK
| 2015-11-08 23:00 | 8 | 1262.0627 | 41.5356 | 12.6142 | 2.359 | 7 | 1.2915 | 23.9877 | 3.0468 | 56.5876 | 59.6343 | 8.5192 | OK
| 2015-11-09 | 9 | 1256.6353 | 41.7464 | 12.6011 | 2.359 | 7 | 1.2971 | 24.0664 | 3.0599 | 56.7731 | 59.833 | 8.5476 | OK
| 2015-11-09 01:00 | 9 | 1254.657 | 42.2034 | 12.6013 | 2.359 | 7 | 1.2992 | 24.1047 | 3.0647 | 56.8634 | 59.9281 | 8.5612 | OK
| 2015-11-09 02:00 | 9 | 1253.0492 | 42.2034 | 12.6002 | 2.359 | 7 | 1.3008 | 24.1335 | 3.0687 | 56.9314 | 60.0001 | 8.5714 | OK
| 2015-11-09 03:00 | 9 | 1252.9746 | 42.2034 | 12.5939 | 2.359 | 7 | 1.3009 | 24.1229 | 3.0689 | 56.9065 | 59.9754 | 8.5679 | OK
| 2015-11-09 04:00 | 9 | 1253.3099 | 42.2034 | 12.6058 | 2.359 | 7 | 1.3006 | 24.1392 | 3.068 | 56.945 | 60.013 | 8.5733 | OK
| 2015-11-09 05:00 | 9 | 1254.9652 | 42.2034 | 12.6065 | 2.366 | 7 | 1.2988 | 24.1088 | 3.073 | 57.0409 | 60.1139 | 8.5877 | OK
| 2015-11-09 06:00 | 9 | 1263.6238 | 42.4815 | 12.6062 | 2.366 | 7 | 1.2899 | 23.9429 | 3.052 | 56.6484 | 59.7003 | 8.5286 | OK
| 2015-11-09 07:00 | 9 | 1254.137 | 43.4719 | 12.6042 | 2.366 | 6.65 | 1.2997 | 24.1203 | 3.0751 | 57.068 | 60.1431 | 9.0441 | OK
| 2015-11-09 08:00 | 9 | 1263.9892 | 43.4719 | 12.6031 | 2.366 | 6.65 | 1.2896 | 23.9301 | 3.0511 | 56.618 | 59.6691 | 8.9728 | OK
| 2015-11-09 09:00 | 9 | 1249.1837 | 43.4719 | 12.5924 | 2.366 | 6.65 | 1.3049 | 24.1933 | 3.0872 | 57.2407 | 60.328 | 9.0719 | OK
| 2015-11-09 10:00 | 9 | 1264.6456 | 44.1978 | 12.6056 | 2.366 | 6.3 | 1.2889 | 23.9225 | 3.0495 | 56.6 | 59.6495 | 9.4682 | OK
| 2015-11-09 11:00 | 9 | 1252.323 | 44.4506 | 12.5913 | 2.366 | 6.3 | 1.3016 | 24.1305 | 3.0795 | 57.0921 | 60.1716 | 9.551 | OK
| 2015-11-09 12:00 | 9 | 1259.0107 | 44.4506 | 12.5961 | 2.366 | 6.3 | 1.2947 | 24.0115 | 3.0632 | 56.8106 | 59.8737 | 9.5038 | OK
| 2015-11-09 13:00 | 9 | 1246.6764 | 44.4506 | 12.6054 | 2.3663 | 6.3 | 1.3075 | 24.2668 | 3.0939 | 57.4226 | 60.5165 | 9.6058 | OK
| 2015-11-09 14:00 | 9 | 1260.988 | 44.3086 | 12.6032 | 2.2565 | 6.3 | 1.2926 | 23.9873 | 2.9168 | 54.1275 | 57.0443 | 9.0547 | OK
| 2015-11-09 15:00 | 9 | 1250.6278 | 43.5955 | 12.6069 | 2.2565 | 6.65 | 1.3033 | 24.193 | 2.941 | 54.5916 | 57.5326 | 8.6515 | OK
| 2015-11-09 16:00 | 9 | 1259.6049 | 43.3013 | 12.5968 | 2.3524 | 6.65 | 1.2941 | 24.0014 | 3.0441 | 56.4605 | 59.5046 | 8.9481 | OK
| 2015-11-09 17:00 | 9 | 1254.4362 | 42.8641 | 12.5985 | 2.2356 | 6.65 | 1.2994 | 24.1035 | 2.905 | 53.8867 | 56.7917 | 8.5401 | OK
| 2015-11-09 18:00 | 9 | 1251.0005 | 42.8641 | 12.6112 | 2.2356 | 6.65 | 1.303 | 24.1941 | 2.9129 | 54.0891 | 57.0021 | 8.5717 | OK
| 2015-11-09 19:00 | 9 | 1259.9251 | 42.027 | 12.6087 | 2.2974 | 7 | 1.2937 | 24.018 | 2.9722 | 55.1786 | 58.1508 | 8.3073 | OK
| 2015-11-09 20:00 | 9 | 1281.4405 | 41.1576 | 12.6054 | 2.2974 | 7 | 1.272 | 23.6086 | 2.9223 | 54.2379 | 57.1601 | 8.1657 | OK
| 2015-11-09 21:00 | 9 | 1353.6906 | 41.1576 | 12.6059 | 2.2974 | 7 | 1.2041 | 22.3495 | 2.7663 | 51.3452 | 54.1115 | 7.7302 | OK
| 2015-11-09 22:00 | 9 | 1347.6675 | 41.1576 | 12.596 | 2.2974 | 7 | 1.2095 | 22.4316 | 2.7787 | 51.534 | 54.3127 | 7.759 | OK
1 | 2015-11-09 23:00 | 9 | 1354.3598 | 41.1576 | 12.6063 | 2.2974 | 7 | 1.2035 | 22.339 | 2.7649 | 51.3213 | 54.0862 | 7.7266 | OK
| 2015-11-10 | 10 | 1343.5655 | 41.1576 | 12.604 | 2.2974 | 7 | 1.2132 | 22.5144 | 2.7872 | 51.7242 | 54.5114 | 7.7873 | OK
| 2015-11-10 01:00 | 10 | 1351.1639 | 41.1576 | 12.6156 | 2.2974 | 7 | 1.2064 | 22.4084 | 2.7715 | 51.4807 | 54.2521 | 7.7503 | OK
| 2015-11-10 02:00 | 10 | 1352.8904 | 41.1576 | 12.6078 | 2.2974 | 7 | 1.2048 | 22.366 | 2.7679 | 51.3832 | 54.1511 | 7.7359 | OK
| 2015-11-10 03:00 | 10 | 1352.1282 | 41.3001 | 12.6058 | 2.3591 | 7 | 1.2055 | 22.3751 | 2.8439 | 52.7856 | 55.6296 | 7.9471 | OK
| 2015-11-10 04:00 | 10 | 1345.42 | 41.3908 | 12.5915 | 2.3591 | 7 | 1.2115 | 22.4611 | 2.8581 | 52.9887 | 55.8468 | 7.9781 | OK
| 2015-11-10 05:00 | 10 | 1343.4633 | 41.3908 | 12.6038 | 2.3591 | 7 | 1.2133 | 22.5158 | 2.8623 | 53.1177 | 55.98 | 7.9971 | OK
| 2015-11-10 06:00 | 10 | 1349.8492 | 41.3908 | 12.6 | 2.3591 | 7 | 1.2075 | 22.4025 | 2.8487 | 52.8504 | 55.6991 | 7.957 | OK
| 2015-11-10 07:00 | 10 | 1336.041 | 41.0762 | 12.5968 | 2.3591 | 7 | 1.22 | 22.6282 | 2.8782 | 53.3829 | 56.261 | 8.0373 | OK
| 2015-11-10 08:00 | 10 | 1351.6436 | 41.1736 | 12.6062 | 2.3591 | 7 | 1.2059 | 22.3839 | 2.845 | 52.8064 | 55.6513 | 7.9502 | OK
| 2015-11-10 09:00 | 10 | 1350.0526 | 41.6102 | 12.6002 | 2.3591 | 7 | 1.2074 | 22.3995 | 2.8483 | 52.8433 | 55.6917 | 7.956 | OK
| 2015-11-10 10:00 | 10 | 1349.0312 | 42.9419 | 12.6038 | 2.373 | 6.65 | 1.2083 | 22.4228 | 2.8673 | 53.2102 | 56.0775 | 8.4327 | OK
| 2015-11-10 11:00 | 10 | 1347.544 | 42.9419 | 12.6054 | 2.2014 | 6.65 | 1.2096 | 22.4505 | 2.6628 | 49.4223 | 52.0851 | 7.8323 | OK
| 2015-11-10 12:00 | 10 | 1351.1531 | 42.9419 | 12.6033 | 2.4967 | 6.65 | 1.2064 | 22.3868 | 3.012 | 55.8941 | 58.9061 | 8.8581 | OK
| 2015-11-10 13:00 | 10 | 1350.4801 | 42.9419 | 12.6004 | 2.1327 | 6.65 | 1.207 | 22.3927 | 2.5741 | 47.7566 | 50.3307 | 7.5685 | OK
| 2015-11-10 14:00 | 10 | 1343.8537 | 42.9419 | 12.6019 | 2.3937 | 6.65 | 1.2129 | 22.5058 | 2.9034 | 53.8719 | 56.7753 | 8.5376 | OK
| 2015-11-10 15:00 | 10 | 1346.6002 | 42.9419 | 12.6083 | 2.3937 | 6.65 | 1.2105 | 22.4713 | 2.8975 | 53.7895 | 56.6869 | 8.5244 | OK
| 2015-11-10 16:00 | 10 | 1348.9543 | 43.1473 | 12.5941 | 2.3937 | 6.65 | 1.2083 | 22.4069 | 2.8924 | 53.6351 | 56.5275 | 8.5004 | OK
| 2015-11-10 17:00 | 10 | 1356.5952 | 43.168 | 12.6019 | 2.3937 | 6.65 | 1.2015 | 22.2945 | 2.8761 | 53.3663 | 56.2424 | 8.4575 | OK
| 2015-11-10 18:00 | 10 | 1348.346 | 43.168 | 12.6054 | 2.3937 | 6.65 | 1.2089 | 22.4372 | 2.8937 | 53.7077 | 56.6014 | 8.5115 | OK
| 2015-11-10 19:00 | 10 | 1351.5551 | 43.168 | 12.6162 | 2.3937 | 6.65 | 1.206 | 22.4031 | 2.8868 | 53.6261 | 56.5129 | 8.4982 | OK
| 2015-11-10 20:00 | 10 | 1610.4709 | 43.168 | 12.6019 | 2.5516 | 6.65 | 1.0121 | 18.78 | 2.5826 | 47.9199 | 50.5025 | 7.5944 | OK
1 | 2015-11-10 21:00 | 10 | 1707.3327 | 43.168 | 12.6023 | 2.5516 | 6.65 | 0.95471 | 17.715 | 2.4361 | 45.2024 | 47.6385 | 7.1637 | OK
| 2015-11-10 22:00 | 10 | 1703.889 | 43.168 | 12.599 | 2.5516 | 6.65 | 0.95664 | 17.7462 | 2.441 | 45.2821 | 47.7231 | 7.1764 | OK
| 2015-11-10 23:00 | 10 | 1504.75 | 43.168 | 12.6148 | 2.5516 | 6.65 | 1.0832 | 20.1199 | 2.764 | 51.3389 | 54.103 | 8.1358 | OK
| 2015-11-11 | 11 | 1440.4605 | 41.0295 | 12.5979 | 2.5516 | 7 | 1.1316 | 20.9898 | 2.8874 | 53.5586 | 56.446 | 8.0637 | OK
| 2015-11-11 01:00 | 11 | 1436.3823 | 40.889 | 12.6137 | 2.5516 | 7.7875 | 1.1348 | 21.0757 | 2.8956 | 53.7777 | 56.6733 | 7.2775 | OK
| 2015-11-11 02:00 | 11 | 1445.477 | 40.889 | 12.6151 | 2.5516 | 7.7875 | 1.1277 | 20.9455 | 2.8774 | 53.4455 | 56.3229 | 7.2325 | OK
| 2015-11-11 03:00 | 11 | 1440.2041 | 40.889 | 12.6007 | 2.5516 | 7.7875 | 1.1318 | 20.9981 | 2.8879 | 53.5798 | 56.4677 | 7.2511 | OK
| 2015-11-11 04:00 | 11 | 1441.8412 | 40.889 | 12.6052 | 2.4899 | 7.7875 | 1.1305 | 20.9819 | 2.8148 | 52.2428 | 55.0577 | 7.07 | OK
| 2015-11-11 05:00 | 11 | 1435.5568 | 40.889 | 12.6061 | 2.4899 | 7.7875 | 1.1354 | 21.0752 | 2.8271 | 52.4751 | 55.3022 | 7.1014 | OK
| 2015-11-11 06:00 | 11 | 1447.0283 | 40.889 | 12.6058 | 2.4899 | 7.7875 | 1.1264 | 20.9076 | 2.8047 | 52.0579 | 54.8626 | 7.045 | OK
| 2015-11-11 07:00 | 11 | 1440.9818 | 40.889 | 12.6043 | 2.4899 | 7.7875 | 1.1312 | 20.9929 | 2.8165 | 52.2703 | 55.0868 | 7.0737 | OK
| 2015-11-11 08:00 | 11 | 1447.5712 | 41.0459 | 12.602 | 2.4899 | 7 | 1.126 | 20.8935 | 2.8037 | 52.0228 | 54.8265 | 7.8324 | OK
| 2015-11-11 09:00 | 11 | 1443.5802 | 42.386 | 12.6068 | 2.4899 | 7 | 1.1291 | 20.9593 | 2.8114 | 52.1865 | 54.998 | 7.8569 | OK
| 2015-11-11 10:00 | 11 | 1433.0587 | 42.8783 | 12.5968 | 2.4899 | 6.65 | 1.1374 | 21.0963 | 2.8321 | 52.5277 | 55.3598 | 8.3248 | OK
| 2015-11-11 11:00 | 11 | 1447.1967 | 42.5595 | 12.6023 | 2.4899 | 7 | 1.1263 | 20.8994 | 2.8044 | 52.0373 | 54.8417 | 7.8345 | OK
| 2015-11-11 12:00 | 11 | 1441.614 | 41.4014 | 12.6038 | 2.5379 | 7 | 1.1307 | 20.9828 | 2.8696 | 53.2533 | 56.1229 | 8.0176 | OK
| 2015-11-11 13:00 | 11 | 1446.9665 | 41.4014 | 12.606 | 2.5379 | 7 | 1.1265 | 20.9089 | 2.859 | 53.0657 | 55.9247 | 7.9892 | OK
| 2015-11-11 14:00 | 11 | 1430.4582 | 41.4014 | 12.6047 | 2.5379 | 7 | 1.1395 | 21.1479 | 2.892 | 53.6724 | 56.5643 | 8.0806 | OK
| 2015-11-11 15:00 | 11 | 1444.0465 | 41.4014 | 12.6103 | 2.5379 | 7 | 1.1288 | 20.9583 | 2.8648 | 53.1911 | 56.0558 | 8.008 | OK
| 2015-11-11 16:00 | 11 | 1432.251 | 41.4014 | 12.5953 | 2.5379 | 7 | 1.1381 | 21.1057 | 2.8884 | 53.5651 | 56.4534 | 8.0648 | OK
| 2015-11-11 17:00 | 11 | 1449.3828 | 41.4014 | 12.6203 | 2.5379 | 7 | 1.1246 | 20.8977 | 2.8542 | 53.0372 | 55.8914 | 7.9845 | OK
| 2015-11-11 18:00 | 11 | 1508.2043 | 41.4014 | 12.5989 | 2.4898 | 7 | 1.0808 | 20.0485 | 2.6909 | 49.9166 | 52.6075 | 7.5154 | OK
| 2015-11-11 19:00 | 11 | 1574.7065 | 41.0667 | 12.6063 | 2.4898 | 7 | 1.0351 | 19.2132 | 2.5772 | 47.8369 | 50.4142 | 7.202 | OK
| 2015-11-11 20:00 | 11 | 1586.7402 | 39.9951 | 12.6031 | 2.4898 | 7.7875 | 1.0273 | 19.0626 | 2.5577 | 47.462 | 50.0196 | 6.4231 | OK
| 2015-11-11 21:00 | 11 | 1580.9338 | 39.9951 | 12.6004 | 2.4898 | 7.7875 | 1.031 | 19.1285 | 2.5671 | 47.626 | 50.193 | 6.4453 | OK
1 | 2015-11-11 22:00 | 11 | 1590.128 | 39.9951 | 12.5993 | 2.4898 | 7.7875 | 1.0251 | 19.0163 | 2.5522 | 47.3466 | 49.8988 | 6.4076 | OK
| 2015-11-11 23:00 | 11 | 1574.792 | 39.9951 | 12.6 | 2.4898 | 7.7875 | 1.0351 | 19.2026 | 2.5771 | 47.8104 | 50.3875 | 6.4703 | OK
| 2015-11-12 | 12 | 1583.5087 | 39.9951 | 12.6082 | 2.4898 | 7.7875 | 1.0294 | 19.1092 | 2.5629 | 47.5779 | 50.1408 | 6.4386 | OK
| 2015-11-12 01:00 | 12 | 1577.3088 | 39.9951 | 12.6032 | 2.359 | 7.7875 | 1.0334 | 19.1768 | 2.4378 | 45.2384 | 47.6762 | 6.1221 | OK
1 | 2015-11-12 02:00 | 12 | 1588.2092 | 40.0001 | 12.5996 | 2.359 | 7.7875 | 1.0263 | 19.0397 | 2.4211 | 44.915 | 47.3361 | 6.0785 | OK
| 2015-11-12 03:00 | 12 | 1584.626 | 40.0446 | 12.6012 | 2.359 | 7.7875 | 1.0286 | 19.0851 | 2.4266 | 45.0222 | 47.4488 | 6.0929 | OK
| 2015-11-12 04:00 | 12 | 1583.7024 | 40.0446 | 12.5994 | 2.359 | 7.7875 | 1.0292 | 19.0936 | 2.428 | 45.0421 | 47.4701 | 6.0957 | OK
| 2015-11-12 05:00 | 12 | 1252.0639 | 40.0446 | 12.61 | 2.359 | 7.7875 | 1.3019 | 24.1712 | 3.0711 | 57.0204 | 60.0915 | 7.7164 | OK
| 2015-11-12 06:00 | 12 | 1259.2423 | 40.0446 | 12.6006 | 2.5721 | 7.7875 | 1.2944 | 24.0156 | 3.3294 | 61.7702 | 65.0996 | 8.3595 | OK
| 2015-11-12 07:00 | 12 | 1434.2611 | 40.0793 | 12.6075 | 2.5721 | 7.7875 | 1.1365 | 21.0967 | 2.9231 | 54.2624 | 57.1855 | 7.3432 | OK
| 2015-11-12 08:00 | 12 | 1444.1741 | 40.6382 | 12.6143 | 2.5721 | 7.7875 | 1.1287 | 20.9631 | 2.903 | 53.9189 | 56.822 | 7.2966 | OK
| 2015-11-12 09:00 | 12 | 1444.9094 | 41.0368 | 12.6099 | 2.5583 | 7 | 1.1281 | 20.9451 | 2.886 | 53.5834 | 56.4694 | 8.0671 | OK
| 2015-11-12 10:00 | 12 | 1438.4058 | 41.8854 | 12.6044 | 2.5583 | 7 | 1.1332 | 21.0306 | 2.899 | 53.8022 | 56.7013 | 8.1002 | OK
| 2015-11-12 11:00 | 12 | 1440.4857 | 41.8854 | 12.6164 | 2.5583 | 7 | 1.1316 | 21.0202 | 2.8949 | 53.7754 | 56.6703 | 8.0958 | OK
| 2015-11-12 12:00 | 12 | 1441.632 | 41.8854 | 12.6126 | 2.5583 | 7 | 1.1307 | 20.9973 | 2.8926 | 53.7169 | 56.6094 | 8.0871 | OK
| 2015-11-12 13:00 | 12 | 1442.6042 | 41.2838 | 12.611 | 2.5583 | 7 | 1.1299 | 20.9804 | 2.8906 | 53.6736 | 56.5642 | 8.0806 | OK
| 2015-11-12 14:00 | 12 | 1440.7226 | 39.7089 | 12.6035 | 2.5583 | 7.7875 | 1.1314 | 20.9952 | 2.8944 | 53.7117 | 56.606 | 7.2688 | OK
| 2015-11-12 15:00 | 12 | 1440.8356 | 39.7089 | 12.6033 | 2.2975 | 7.7875 | 1.1313 | 20.9932 | 2.5991 | 48.2317 | 50.8309 | 6.5272 | OK
| 2015-11-12 16:00 | 12 | 1445.4884 | 39.7089 | 12.6084 | 2.2975 | 7.7875 | 1.1276 | 20.9343 | 2.5908 | 48.0962 | 50.687 | 6.5088 | OK
| 2015-11-12 17:00 | 12 | 1450.4291 | 39.7089 | 12.6292 | 2.5103 | 7.7875 | 1.1238 | 20.8973 | 2.8211 | 52.4594 | 55.2805 | 7.0986 | OK
| 2015-11-12 18:00 | 12 | 1452.8529 | 39.7089 | 12.6136 | 2.5103 | 7.7875 | 1.1219 | 20.8366 | 2.8164 | 52.307 | 55.1234 | 7.0784 | OK
| 2015-11-12 19:00 | 12 | 1444.4402 | 39.7089 | 12.6123 | 2.5103 | 7.7875 | 1.1285 | 20.9558 | 2.8328 | 52.6062 | 55.439 | 7.119 | OK
| 2015-11-12 20:00 | 12 | 1449.6738 | 39.7089 | 12.6101 | 2.5103 | 7.7875 | 1.1244 | 20.8766 | 2.8226 | 52.4072 | 55.2298 | 7.0921 | OK
| 2015-11-12 21:00 | 12 | 1444.8992 | 39.9388 | 12.5917 | 2.5103 | 7.7875 | 1.1281 | 20.9151 | 2.8319 | 52.5039 | 55.3358 | 7.1057 | OK
| 2015-11-12 22:00 | 12 | 1444.4538 | 40.2319 | 12.5983 | 2.4001 | 7.7875 | 1.1285 | 20.9325 | 2.7084 | 50.2404 | 52.9488 | 6.7992 | OK
| 2015-11-12 23:00 | 12 | 1438.1815 | 40.2319 | 12.6072 | 2.4001 | 7.7875 | 1.1334 | 21.0386 | 2.7202 | 50.495 | 53.2152 | 6.8334 | OK
| 2015-11-13 | 13 | 1437.5652 | 40.2319 | 12.6056 | 2.4001 | 7.7875 | 1.1339 | 21.0449 | 2.7214 | 50.51 | 53.2314 | 6.8355 | OK
| 2015-11-13 01:00 | 13 | 1436.7761 | 40.2319 | 12.6096 | 2.4001 | 7.7875 | 1.1345 | 21.0632 | 2.7229 | 50.5541 | 53.277 | 6.8413 | OK
| 2015-11-13 02:00 | 13 | 1440.3492 | 40.2319 | 12.6131 | 2.4001 | 7.7875 | 1.1317 | 21.0168 | 2.7161 | 50.4427 | 53.1588 | 6.8262 | OK
| 2015-11-13 03:00 | 13 | 1453.9133 | 40.2319 | 12.5969 | 2.4001 | 7.7875 | 1.1211 | 20.794 | 2.6908 | 49.9079 | 52.5987 | 6.7542 | OK
| 2015-11-13 04:00 | 13 | 1445.2275 | 40.2782 | 12.6177 | 2.4001 | 7.7875 | 1.1279 | 20.9535 | 2.707 | 50.2907 | 52.9977 | 6.8055 | OK
| 2015-11-13 05:00 | 13 | 1447.4203 | 40.3449 | 12.6154 | 2.4001 | 7.7875 | 1.1261 | 20.9178 | 2.7029 | 50.2052 | 52.9081 | 6.794 | OK
| 2015-11-13 06:00 | 13 | 1445.0908 | 40.3449 | 12.6162 | 2.5172 | 7.7875 | 1.128 | 20.953 | 2.8393 | 52.7426 | 55.5819 | 7.1373 | OK
| 2015-11-13 07:00 | 13 | 1445.2035 | 40.3449 | 12.6054 | 2.2973 | 7.7875 | 1.1279 | 20.9333 | 2.591 | 48.0896 | 50.6807 | 6.508 | OK
| 2015-11-13 08:00 | 13 | 1439.7049 | 40.2075 | 12.5973 | 2.5172 | 7.7875 | 1.1322 | 20.9998 | 2.8499 | 52.8603 | 55.7102 | 7.1538 | OK
| 2015-11-13 09:00 | 13 | 1436.5511 | 40.2111 | 12.6163 | 2.5035 | 7.7875 | 1.1347 | 21.0776 | 2.8406 | 52.7675 | 55.6081 | 7.1407 | OK
| 2015-11-13 10:00 | 13 | 1440.4893 | 40.7937 | 12.6107 | 2.5035 | 7.7875 | 1.1316 | 21.0107 | 2.8328 | 52.6 | 55.4329 | 7.1182 | OK
| 2015-11-13 11:00 | 13 | 1453.165 | 40.7937 | 12.6076 | 2.5035 | 7.7875 | 1.1217 | 20.8222 | 2.8081 | 52.1282 | 54.9364 | 7.0544 | OK
| 2015-11-13 12:00 | 13 | 1445.5905 | 40.7937 | 12.6005 | 2.4833 | 7.7875 | 1.1276 | 20.9197 | 2.8 | 51.949 | 54.7491 | 7.0304 | OK
| 2015-11-13 13:00 | 13 | 1432.9843 | 40.7937 | 12.6016 | 2.4833 | 7.7875 | 1.1375 | 21.1055 | 2.8247 | 52.4104 | 55.2351 | 7.0928 | OK
| 2015-11-13 14:00 | 13 | 1439.2839 | 40.7937 | 12.6089 | 2.4833 | 7.7875 | 1.1325 | 21.0253 | 2.8123 | 52.2113 | 55.0236 | 7.0656 | OK
| 2015-11-13 15:00 | 13 | 1446.1418 | 40.7869 | 12.6001 | 2.4833 | 7.7875 | 1.1271 | 20.9111 | 2.799 | 51.9277 | 54.7266 | 7.0275 | OK
| 2015-11-13 16:00 | 13 | 1451.0568 | 38.9952 | 12.6091 | 2.4833 | 8.575 | 1.1233 | 20.855 | 2.7895 | 51.7884 | 54.5779 | 6.3648 | OK
| 2015-11-13 17:00 | 13 | 1439.4728 | 38.9952 | 12.602 | 2.4833 | 8.575 | 1.1324 | 21.011 | 2.8119 | 52.1758 | 54.9877 | 6.4126 | OK
1 | 2015-11-13 18:00 | 13 | 1445.2369 | 38.9952 | 12.6011 | 2.2699 | 8.575 | 1.1278 | 20.9257 | 2.5601 | 47.4988 | 50.0588 | 5.8378 | OK
| 2015-11-13 19:00 | 13 | 1435.8317 | 38.9952 | 12.6035 | 2.4484 | 8.575 | 1.1352 | 21.0668 | 2.7795 | 51.5795 | 54.3589 | 6.3392 | OK
| 2015-11-13 20:00 | 13 | 1446.3735 | 38.9952 | 12.6115 | 2.4484 | 8.575 | 1.127 | 20.9266 | 2.7592 | 51.2362 | 53.9954 | 6.2968 | OK
| 2015-11-13 21:00 | 13 | 1448.1573 | 38.9952 | 12.5994 | 2.4484 | 8.575 | 1.1256 | 20.8808 | 2.7558 | 51.1241 | 53.8799 | 6.2834 | OK
| 2015-11-13 22:00 | 13 | 1439.808 | 38.9952 | 12.6089 | 2.4484 | 8.575 | 1.1321 | 21.0176 | 2.7718 | 51.4591 | 54.2309 | 6.3243 | OK
| 2015-11-13 23:00 | 13 | 1438.3973 | 39.0249 | 12.5975 | 2.4484 | 8.575 | 1.1332 | 21.0192 | 2.7745 | 51.4629 | 54.2374 | 6.3251 | OK
| 2015-11-14 | 14 | 1442.3731 | 40.7301 | 12.6023 | 2.4484 | 7.7875 | 1.1301 | 20.9693 | 2.7669 | 51.3409 | 54.1077 | 6.948 | OK
| 2015-11-14 01:00 | 14 | 1447.0166 | 40.7301 | 12.6037 | 2.4484 | 7.7875 | 1.1265 | 20.9043 | 2.758 | 51.1815 | 53.9395 | 6.9264 | OK
| 2015-11-14 02:00 | 14 | 1436.1407 | 40.7301 | 12.6071 | 2.4484 | 7.7875 | 1.135 | 21.0682 | 2.7789 | 51.583 | 54.3619 | 6.9807 | OK
| 2015-11-14 03:00 | 14 | 1445.2603 | 40.7301 | 12.6053 | 2.4964 | 7.7875 | 1.1278 | 20.9324 | 2.8155 | 52.2563 | 55.0718 | 7.0718 | OK
| 2015-11-14 04:00 | 14 | 1437.2052 | 40.7301 | 12.6019 | 2.4964 | 7.7875 | 1.1341 | 21.0439 | 2.8313 | 52.5346 | 55.3659 | 7.1096 | OK
| 2015-11-14 05:00 | 14 | 1437.1011 | 40.7301 | 12.6053 | 2.483 | 7.7875 | 1.1342 | 21.0512 | 2.8163 | 52.2712 | 55.0876 | 7.0738 | OK
| 2015-11-14 06:00 | 14 | 1437.585 | 40.7301 | 12.6063 | 2.3936 | 7.7875 | 1.1338 | 21.0458 | 2.714 | 50.3749 | 53.0888 | 6.8172 | OK
| 2015-11-14 07:00 | 14 | 1440.5701 | 40.7282 | 12.6021 | 2.3936 | 7.7875 | 1.1315 | 20.9952 | 2.7083 | 50.2538 | 52.9622 | 6.8009 | OK
| 2015-11-14 08:00 | 14 | 1442.3305 | 40.7195 | 12.5902 | 2.3936 | 7.7875 | 1.1301 | 20.9498 | 2.705 | 50.1451 | 52.8501 | 6.7865 | OK
| 2015-11-14 09:00 | 14 | 1438.5991 | 40.7195 | 12.6013 | 2.3936 | 7.7875 | 1.133 | 21.0227 | 2.712 | 50.3196 | 53.0316 | 6.8098 | OK
| 2015-11-14 10:00 | 14 | 1444.977 | 40.7195 | 12.6009 | 2.3936 | 7.7875 | 1.128 | 20.9292 | 2.7001 | 50.0959 | 52.7959 | 6.7796 | OK
| 2015-11-14 11:00 | 14 | 1448.5798 | 40.6128 | 12.6016 | 2.3936 | 7.7875 | 1.1252 | 20.8783 | 2.6934 | 49.974 | 52.6674 | 6.7631 | OK
| 2015-11-14 12:00 | 14 | 1447.3761 | 40.5039 | 12.612 | 2.3936 | 7.7875 | 1.1262 | 20.9128 | 2.6956 | 50.0566 | 52.7522 | 6.774 | OK
| 2015-11-14 13:00 | 14 | 1435.6834 | 40.5039 | 12.6058 | 2.4826 | 7.7875 | 1.1353 | 21.0729 | 2.8186 | 52.316 | 55.1346 | 7.0799 | OK
| 2015-11-14 14:00 | 14 | 1453.901 | 40.5039 | 12.6034 | 2.4763 | 7.7875 | 1.1211 | 20.8049 | 2.7762 | 51.5192 | 54.2955 | 6.9721 | OK
| 2015-11-14 15:00 | 14 | 1740.7062 | 40.2862 | 12.5988 | 2.4006 | 7.7875 | 0.9364 | 17.3706 | 2.248 | 41.7007 | 43.9487 | 5.6435 | OK
| 2015-11-14 16:00 | 14 | 1805.3847 | 39.5782 | 12.6141 | 2.4006 | 7.7875 | 0.90285 | 16.7686 | 2.1674 | 40.2555 | 42.4229 | 5.4476 | OK
1 | 2015-11-14 17:00 | 14 | 1807.0734 | 39.5782 | 12.5995 | 2.4006 | 7.7875 | 0.90201 | 16.7336 | 2.1654 | 40.1715 | 42.3369 | 5.4365 | OK
| 2015-11-14 18:00 | 14 | 1578.6852 | 39.4563 | 12.6089 | 2.4006 | 7.7875 | 1.0325 | 19.1687 | 2.4787 | 46.0173 | 48.496 | 6.2274 | OK
| 2015-11-14 19:00 | 14 | 1455.6171 | 38.1155 | 12.6105 | 2.2217 | 8.575 | 1.1198 | 20.792 | 2.4879 | 46.1941 | 48.6819 | 5.6772 | OK
| 2015-11-14 20:00 | 14 | 1444.3456 | 38.1155 | 12.6089 | 2.2217 | 8.575 | 1.1285 | 20.9517 | 2.5073 | 46.5488 | 49.0561 | 5.7208 | OK
| 2015-11-14 21:00 | 14 | 1428.5148 | 38.1155 | 12.6098 | 2.2217 | 8.575 | 1.141 | 21.1852 | 2.5351 | 47.0678 | 49.6028 | 5.7846 | OK
| 2015-11-14 22:00 | 14 | 1435.7512 | 39.9922 | 12.61 | 2.2217 | 7.7875 | 1.1353 | 21.0789 | 2.5223 | 46.8314 | 49.3537 | 6.3376 | OK
| 2015-11-14 23:00 | 14 | 1442.8605 | 40.0163 | 12.6026 | 2.4623 | 7.7875 | 1.1297 | 20.9627 | 2.7816 | 51.6163 | 54.398 | 6.9853 | OK
| 2015-11-15 | 15 | 1440.3102 | 40.0163 | 12.6033 | 2.4623 | 7.7875 | 1.1317 | 21.0009 | 2.7866 | 51.7103 | 54.4969 | 6.998 | OK
| 2015-11-15 01:00 | 15 | 1446.932 | 40.0163 | 12.6014 | 2.4623 | 7.7875 | 1.1265 | 20.9017 | 2.7738 | 51.4661 | 54.2399 | 6.965 | OK
| 2015-11-15 02:00 | 15 | 1447.2476 | 40.039 | 12.6179 | 2.4623 | 7.7875 | 1.1263 | 20.9246 | 2.7732 | 51.5224 | 54.2956 | 6.9721 | OK
1 | 2015-11-15 03:00 | 15 | 1448.3573 | 40.7972 | 12.6069 | 2.3866 | 7.7875 | 1.1254 | 20.8903 | 2.6859 | 49.8574 | 52.5433 | 6.7471 | OK
| 2015-11-15 04:00 | 15 | 1446.4813 | 40.7972 | 12.607 | 2.3866 | 7.7875 | 1.1269 | 20.9175 | 2.6894 | 49.9222 | 52.6117 | 6.7559 | OK
| 2015-11-15 05:00 | 15 | 1444.5799 | 40.7972 | 12.6146 | 2.3866 | 7.7875 | 1.1284 | 20.9577 | 2.693 | 50.0183 | 52.7113 | 6.7687 | OK
| 2015-11-15 06:00 | 15 | 1444.0109 | 40.7972 | 12.6103 | 2.3866 | 7.7875 | 1.1288 | 20.9588 | 2.694 | 50.0209 | 52.7149 | 6.7692 | OK
| 2015-11-15 07:00 | 15 | 1442.7086 | 41.1131 | 12.5993 | 2.3866 | 7 | 1.1298 | 20.9594 | 2.6965 | 50.0224 | 52.7188 | 7.5313 | OK
| 2015-11-15 08:00 | 15 | 1441.5494 | 42.3483 | 12.6015 | 2.4487 | 7 | 1.1307 | 20.9799 | 2.7688 | 51.3735 | 54.1423 | 7.7346 | OK
| 2015-11-15 09:00 | 15 | 1446.2769 | 42.3483 | 12.6078 | 2.3043 | 7 | 1.127 | 20.9218 | 2.5971 | 48.211 | 50.8081 | 7.2583 | OK
| 2015-11-15 10:00 | 15 | 1445.9237 | 42.3483 | 12.6057 | 2.3043 | 7 | 1.1273 | 20.9235 | 2.5977 | 48.2148 | 50.8125 | 7.2589 | OK
| 2015-11-15 11:00 | 15 | 1444.5533 | 42.3483 | 12.595 | 2.3043 | 7 | 1.1284 | 20.9255 | 2.6002 | 48.2195 | 50.8196 | 7.2599 | OK
| 2015-11-15 12:00 | 15 | 1453.3749 | 42.3483 | 12.6042 | 2.3043 | 7 | 1.1215 | 20.8137 | 2.5844 | 47.9617 | 50.5461 | 7.2209 | OK
| 2015-11-15 13:00 | 15 | 1444.6138 | 42.3483 | 12.5963 | 2.3043 | 7 | 1.1283 | 20.9269 | 2.6001 | 48.2225 | 50.8226 | 7.2604 | OK
| 2015-11-15 14:00 | 15 | 1446.7163 | 42.3483 | 12.6027 | 2.3043 | 7 | 1.1267 | 20.907 | 2.5963 | 48.1767 | 50.773 | 7.2533 | OK
| 2015-11-15 15:00 | 15 | 1439.4649 | 42.1373 | 12.6111 | 2.4695 | 7 | 1.1324 | 21.0263 | 2.7963 | 51.9237 | 54.72 | 7.8171 | OK
| 2015-11-15 16:00 | 15 | 1446.3298 | 41.412 | 12.6061 | 2.4695 | 7 | 1.127 | 20.9182 | 2.7831 | 51.6567 | 54.4397 | 7.7771 | OK
| 2015-11-15 17:00 | 15 | 1453.4707 | 41.412 | 12.6076 | 2.4695 | 7 | 1.1215 | 20.8179 | 2.7694 | 51.4089 | 54.1783 | 7.7398 | OK
| 2015-11-15 18:00 | 15 | 1445.069 | 41.412 | 12.5951 | 2.3591 | 7 | 1.128 | 20.9183 | 2.661 | 49.3488 | 52.0099 | 7.43 | OK
| 2015-11-15 19:00 | 15 | 1450.6018 | 41.412 | 12.6157 | 2.4349 | 7 | 1.1237 | 20.8725 | 2.736 | 50.8224 | 53.5584 | 7.6512 | OK
| 2015-11-15 20:00 | 15 | 1446.2381 | 41.412 | 12.6067 | 2.4349 | 7 | 1.1271 | 20.9205 | 2.7443 | 50.9391 | 53.6834 | 7.6691 | OK
| 2015-11-15 21:00 | 15 | 1456.9348 | 41.412 | 12.5985 | 2.2767 | 7 | 1.1188 | 20.7535 | 2.5472 | 47.25 | 49.7972 | 7.1139 | OK
| 2015-11-15 22:00 | 15 | 1440.1542 | 41.412 | 12.5971 | 2.3729 | 7 | 1.1318 | 20.9929 | 2.6857 | 49.8147 | 52.5005 | 7.5001 | OK
| 2015-11-15 23:00 | 15 | 1439.9045 | 41.0251 | 12.6108 | 2.3729 | 7 | 1.132 | 21.0194 | 2.6862 | 49.8776 | 52.5638 | 7.5091 | OK
| 2015-11-16 | 16 | 1439.7311 | 40.0411 | 12.6111 | 2.3729 | 7.7875 | 1.1322 | 21.0225 | 2.6865 | 49.885 | 52.5715 | 6.7508 | OK
| 2015-11-16 01:00 | 16 | 1438.8839 | 40.0411 | 12.5976 | 2.3729 | 7.7875 | 1.1328 | 21.0123 | 2.6881 | 49.8608 | 52.5489 | 6.7478 | OK
1 | 2015-11-16 02:00 | 16 | 1450.7091 | 40.0411 | 12.6037 | 2.3729 | 7.7875 | 1.1236 | 20.8511 | 2.6662 | 49.4783 | 52.1445 | 6.6959 | OK
| 2015-11-16 03:00 | 16 | 1447.8764 | 40.0411 | 12.6042 | 2.3729 | 7.7875 | 1.1258 | 20.8928 | 2.6714 | 49.5772 | 52.2486 | 6.7093 | OK
| 2015-11-16 04:00 | 16 | 1452.9062 | 41.5354 | 12.6035 | 2.3729 | 7 | 1.1219 | 20.8193 | 2.6622 | 49.4027 | 52.0649 | 7.4378 | OK
| 2015-11-16 05:00 | 16 | 1442.0011 | 41.79 | 12.6149 | 2.3729 | 7 | 1.1304 | 20.9957 | 2.6823 | 49.8214 | 52.5037 | 7.5005 | OK
| 2015-11-16 06:00 | 16 | 1451.8394 | 41.79 | 12.6115 | 2.4074 | 7 | 1.1227 | 20.8477 | 2.7028 | 50.1887 | 52.8915 | 7.5559 | OK
| 2015-11-16 07:00 | 16 | 1439.9437 | 42.4099 | 12.5935 | 2.4074 | 7 | 1.132 | 20.9899 | 2.7251 | 50.5309 | 53.2561 | 7.608 | OK
| 2015-11-16 08:00 | 16 | 1433.8634 | 42.8466 | 12.6029 | 2.4074 | 6.65 | 1.1368 | 21.0948 | 2.7367 | 50.7834 | 53.5201 | 8.0481 | OK
| 2015-11-16 09:00 | 16 | 1444.8285 | 42.1928 | 12.6217 | 2.4074 | 7 | 1.1282 | 20.9659 | 2.7159 | 50.4732 | 53.1891 | 7.5984 | OK
| 2015-11-16 10:00 | 16 | 1443.1763 | 41.6122 | 12.5969 | 2.4074 | 7 | 1.1295 | 20.9486 | 2.719 | 50.4315 | 53.1505 | 7.5929 | OK
| 2015-11-16 11:00 | 16 | 1440.7701 | 40.4439 | 12.622 | 2.4074 | 7.7875 | 1.1313 | 21.0254 | 2.7236 | 50.6163 | 53.3398 | 6.8494 | OK
| 2015-11-16 12:00 | 16 | 1434.6742 | 40.4439 | 12.6064 | 2.4074 | 7.7875 | 1.1361 | 21.0886 | 2.7351 | 50.7685 | 53.5037 | 6.8705 | OK
| 2015-11-16 13:00 | 16 | 1447.7624 | 40.0999 | 12.6179 | 2.4074 | 7.7875 | 1.1259 | 20.9171 | 2.7104 | 50.3556 | 53.066 | 6.8143 | OK
| 2015-11-16 14:00 | 16 | 1452.4862 | 41.5321 | 12.6096 | 2.1464 | 7 | 1.1222 | 20.8353 | 2.4087 | 44.7206 | 47.1293 | 6.7328 | OK
| 2015-11-16 15:00 | 16 | 1451.5318 | 41.8405 | 12.6137 | 2.4417 | 7 | 1.123 | 20.8558 | 2.742 | 50.9245 | 53.6664 | 7.6666 | OK
| 2015-11-16 16:00 | 16 | 1442.7764 | 41.949 | 12.6099 | 2.4417 | 7 | 1.1298 | 20.9761 | 2.7586 | 51.2182 | 53.9768 | 7.711 | OK
| 2015-11-16 17:00 | 16 | 1439.8898 | 41.8692 | 12.6022 | 2.4417 | 7 | 1.132 | 21.0054 | 2.7641 | 51.2897 | 54.0538 | 7.722 | OK
| 2015-11-16 18:00 | 16 | 1431.6326 | 39.7231 | 12.5978 | 2.4417 | 7.7875 | 1.1386 | 21.1191 | 2.7801 | 51.5673 | 54.3474 | 6.9788 | OK
| 2015-11-16 19:00 | 16 | 1442.3092 | 39.7231 | 12.6226 | 2.4417 | 7.7875 | 1.1301 | 21.004 | 2.7595 | 51.2864 | 54.0459 | 6.9401 | OK
| 2015-11-16 20:00 | 16 | 1442.4956 | 39.7231 | 12.6078 | 2.4417 | 7.7875 | 1.13 | 20.9766 | 2.7591 | 51.2194 | 53.9785 | 6.9314 | OK
| 2015-11-16 21:00 | 16 | 1444.5564 | 39.7231 | 12.6172 | 2.4417 | 7.7875 | 1.1284 | 20.9623 | 2.7552 | 51.1844 | 53.9396 | 6.9264 | OK
| 2015-11-16 22:00 | 16 | 1444.2289 | 39.7231 | 12.6039 | 2.4417 | 7.7875 | 1.1286 | 20.945 | 2.7558 | 51.1424 | 53.8982 | 6.9211 | OK
| 2015-11-16 23:00 | 16 | 1462.9875 | 39.7231 | 12.6132 | 2.4762 | 7.7875 | 1.1142 | 20.6916 | 2.7589 | 51.2367 | 53.9955 | 6.9336 | OK
| 2015-11-17 | 17 | 1441.1562 | 39.7231 | 12.61 | 2.4762 | 7.7875 | 1.131 | 20.9998 | 2.8007 | 51.9997 | 54.8003 | 7.037 | OK
| 2015-11-17 01:00 | 17 | 1454.2984 | 39.67 | 12.6176 | 2.4762 | 7.7875 | 1.1208 | 20.8226 | 2.7754 | 51.5608 | 54.3362 | 6.9774 | OK
| 2015-11-17 02:00 | 17 | 1444.6149 | 39.08 | 12.6074 | 2.4762 | 8.575 | 1.1283 | 20.9451 | 2.794 | 51.8644 | 54.6583 | 6.3742 | OK
| 2015-11-17 03:00 | 17 | 1442.9673 | 39.08 | 12.6076 | 2.4762 | 8.575 | 1.1296 | 20.9694 | 2.7972 | 51.9244 | 54.7216 | 6.3815 | OK
| 2015-11-17 04:00 | 17 | 1439.5004 | 39.08 | 12.6125 | 2.4762 | 8.575 | 1.1323 | 21.0282 | 2.8039 | 52.07 | 54.8739 | 6.3993 | OK
| 2015-11-17 05:00 | 17 | 1439.7406 | 39.08 | 12.6029 | 2.4762 | 8.575 | 1.1321 | 21.0086 | 2.8034 | 52.0215 | 54.8249 | 6.3936 | OK
1 | 2015-11-17 06:00 | 17 | 1444.0807 | 39.08 | 12.5971 | 2.4762 | 8.575 | 1.1287 | 20.9358 | 2.795 | 51.8413 | 54.6363 | 6.3716 | OK
| 2015-11-17 07:00 | 17 | 1409.0724 | 39.0708 | 12.6169 | 2.4899 | 8.575 | 1.1568 | 21.4897 | 2.8803 | 53.5072 | 56.3875 | 6.5758 | OK
| 2015-11-17 08:00 | 17 | 1426.1367 | 40.0884 | 12.6122 | 2.4899 | 7.7875 | 1.1429 | 21.2247 | 2.8458 | 52.8473 | 55.6931 | 7.1516 | OK
| 2015-11-17 09:00 | 17 | 1424.2455 | 40.7909 | 12.6179 | 2.4899 | 7.7875 | 1.1445 | 21.2624 | 2.8496 | 52.9412 | 55.7908 | 7.1641 | OK
| 2015-11-17 10:00 | 17 | 1436.4546 | 41.3095 | 12.591 | 2.3525 | 7 | 1.1347 | 21.0367 | 2.6695 | 49.4888 | 52.1583 | 7.4512 | OK
| 2015-11-17 11:00 | 17 | 1432.9837 | 41.3095 | 12.585 | 2.3525 | 7 | 1.1375 | 21.0776 | 2.6759 | 49.585 | 52.2609 | 7.4658 | OK
| 2015-11-17 12:00 | 17 | 1423.841 | 41.3095 | 12.6047 | 2.3525 | 7 | 1.1448 | 21.2463 | 2.6931 | 49.9818 | 52.6749 | 7.525 | OK
| 2015-11-17 13:00 | 17 | 1429.3945 | 41.3095 | 12.6114 | 2.4765 | 7 | 1.1403 | 21.175 | 2.8241 | 52.4403 | 55.2644 | 7.8949 | OK
| 2015-11-17 14:00 | 17 | 1428.8017 | 41.3095 | 12.591 | 2.7926 | 7 | 1.1408 | 21.1495 | 3.1859 | 59.0628 | 62.2487 | 8.8927 | OK
| 2015-11-17 15:00 | 17 | 1440.89 | 41.3095 | 12.6159 | 2.7926 | 7 | 1.1312 | 21.0135 | 3.1592 | 58.6832 | 61.8424 | 8.8346 | OK
| 2015-11-17 16:00 | 17 | 1454.7039 | 39.2237 | 12.6074 | 2.7925 | 7.7875 | 1.1205 | 20.8 | 3.129 | 58.0845 | 61.2136 | 7.8605 | OK
| 2015-11-17 17:00 | 17 | 1440.1624 | 38.4582 | 12.6032 | 2.7925 | 8.575 | 1.1318 | 21.0029 | 3.1606 | 58.6514 | 61.812 | 7.2084 | OK
| 2015-11-17 18:00 | 17 | 1450.2432 | 38.4582 | 12.5969 | 2.7925 | 8.575 | 1.1239 | 20.8466 | 3.1387 | 58.2148 | 61.3534 | 7.1549 | OK
| 2015-11-17 19:00 | 17 | 1442.9631 | 38.4582 | 12.6081 | 2.7925 | 8.575 | 1.1296 | 20.9704 | 3.1545 | 58.5605 | 61.715 | 7.1971 | OK
| 2015-11-17 20:00 | 17 | 1441.882 | 38.4582 | 12.6102 | 2.7925 | 8.575 | 1.1305 | 20.9895 | 3.1569 | 58.6138 | 61.7707 | 7.2036 | OK
| 2015-11-17 21:00 | 17 | 1444.6428 | 38.2818 | 12.608 | 2.7925 | 8.575 | 1.1283 | 20.9458 | 3.1508 | 58.4919 | 61.6428 | 7.1887 | OK
| 2015-11-17 22:00 | 17 | 1449.4343 | 37.7727 | 12.6046 | 2.7925 | 8.575 | 1.1246 | 20.871 | 3.1404 | 58.2828 | 61.4233 | 7.1631 | OK
| 2015-11-17 23:00 | 17 | 1455.9778 | 37.7727 | 12.6045 | 2.7925 | 8.575 | 1.1195 | 20.7769 | 3.1263 | 58.0202 | 61.1465 | 7.1308 | OK
| 2015-11-18 | 18 | 1445.2407 | 37.7727 | 12.5984 | 2.8131 | 8.575 | 1.1278 | 20.9212 | 3.1727 | 58.8531 | 62.0258 | 7.2333 | OK
| 2015-11-18 01:00 | 18 | 1446.4093 | 37.7727 | 12.6043 | 2.8131 | 8.575 | 1.1269 | 20.9141 | 3.1701 | 58.8329 | 62.003 | 7.2307 | OK
| 2015-11-18 02:00 | 18 | 1441.7902 | 37.7727 | 12.6057 | 2.8132 | 8.575 | 1.1305 | 20.9834 | 3.1804 | 59.0303 | 62.2107 | 7.2549 | OK
| 2015-11-18 03:00 | 18 | 1439.6548 | 37.7727 | 12.6091 | 2.7513 | 8.575 | 1.1322 | 21.0203 | 3.1151 | 57.8337 | 60.9488 | 7.1077 | OK
| 2015-11-18 04:00 | 18 | 1439.9402 | 37.7727 | 12.6056 | 2.7445 | 8.575 | 1.132 | 21.0103 | 3.1067 | 57.6623 | 60.7691 | 7.0868 | OK
| 2015-11-18 05:00 | 18 | 1436.6474 | 37.845 | 12.6119 | 2.7445 | 8.575 | 1.1346 | 21.0688 | 3.1139 | 57.8231 | 60.9369 | 7.1063 | OK
| 2015-11-18 06:00 | 18 | 1455.8102 | 38.0059 | 12.6138 | 2.7445 | 8.575 | 1.1197 | 20.7948 | 3.0729 | 57.0709 | 60.1437 | 7.0138 | OK
| 2015-11-18 07:00 | 18 | 1274.5279 | 38.0059 | 12.6325 | 2.7445 | 8.575 | 1.2789 | 23.7877 | 3.5099 | 65.2848 | 68.7948 | 8.0227 | OK
| 2015-11-18 08:00 | 18 | 891.8521 | 38.4805 | 12.6157 | 2.8269 | 8.575 | 1.8277 | 33.9492 | 5.1666 | 95.9703 | 101.1369 | 11.7944 | OK
| 2015-11-18 09:00 | 18 | 1329.7891 | 38.497 | 12.5959 | 2.6895 | 8.575 | 1.2258 | 22.733 | 3.2966 | 61.1399 | 64.4365 | 7.5145 | OK
| 2015-11-18 10:00 | 18 | 1351.0622 | 38.497 | 12.604 | 2.4626 | 8.575 | 1.2065 | 22.3894 | 2.971 | 55.1364 | 58.1075 | 6.7764 | OK
| 2015-11-18 11:00 | 18 | 1346.0608 | 40.0766 | 12.6054 | 2.6894 | 7.7875 | 1.2109 | 22.4753 | 3.2567 | 60.4443 | 63.701 | 8.1799 | OK
| 2015-11-18 12:00 | 18 | 1352.2686 | 40.2531 | 12.6017 | 2.6894 | 7.7875 | 1.2054 | 22.3655 | 3.2417 | 60.1491 | 63.3908 | 8.1401 | OK
| 2015-11-18 13:00 | 18 | 1352.7189 | 40.2531 | 12.6016 | 2.6894 | 7.7875 | 1.205 | 22.3579 | 3.2406 | 60.1286 | 63.3693 | 8.1373 | OK
| 2015-11-18 14:00 | 18 | 1528.179 | 40.2531 | 12.6009 | 2.6894 | 7.7875 | 1.0666 | 19.7896 | 2.8686 | 53.2217 | 56.0902 | 7.2026 | OK
1 | 2015-11-18 15:00 | 18 | 1715.1933 | 40.2531 | 12.5938 | 2.6894 | 7.7875 | 0.95033 | 17.622 | 2.5558 | 47.3922 | 49.948 | 6.4139 | OK
| 2015-11-18 16:00 | 18 | 1701.8268 | 40.0222 | 12.5954 | 2.6894 | 7.7875 | 0.95779 | 17.7626 | 2.5759 | 47.7703 | 50.3461 | 6.465 | OK
| 2015-11-18 17:00 | 18 | 1573.075 | 39.4546 | 12.6094 | 2.6894 | 7.7875 | 1.0362 | 19.2378 | 2.7867 | 51.7377 | 54.5243 | 7.0015 | OK
| 2015-11-18 18:00 | 18 | 1442.1818 | 39.4546 | 12.596 | 2.6069 | 7.7875 | 1.1302 | 20.9615 | 2.9464 | 54.6439 | 57.5903 | 7.3952 | OK
| 2015-11-18 19:00 | 18 | 1437.0706 | 39.4546 | 12.6076 | 2.6069 | 7.7875 | 1.1343 | 21.0554 | 2.9568 | 54.8887 | 57.8455 | 7.428 | OK
| 2015-11-18 20:00 | 18 | 1439.7493 | 39.1922 | 12.6105 | 2.6069 | 8.575 | 1.1321 | 21.0211 | 2.9513 | 54.7992 | 57.7505 | 6.7348 | OK
| 2015-11-18 21:00 | 18 | 1441.3187 | 38.8703 | 12.5966 | 2.6069 | 8.575 | 1.1309 | 20.975 | 2.9481 | 54.6791 | 57.6272 | 6.7204 | OK
| 2015-11-18 22:00 | 18 | 1454.6455 | 39.02 | 12.5979 | 2.6069 | 8.575 | 1.1205 | 20.7852 | 2.9211 | 54.1841 | 57.1052 | 6.6595 | OK
| 2015-11-18 23:00 | 18 | 1445.0166 | 39.02 | 12.597 | 2.6069 | 8.575 | 1.128 | 20.9222 | 2.9406 | 54.5413 | 57.4819 | 6.7034 | OK
| 2015-11-19 | 19 | 1440.9807 | 39.02 | 12.5998 | 2.6069 | 8.575 | 1.1312 | 20.9854 | 2.9488 | 54.7061 | 57.6549 | 6.7236 | OK
| 2015-11-19 01:00 | 19 | 1434.8086 | 39.0004 | 12.6016 | 2.6069 | 8.575 | 1.136 | 21.0786 | 2.9615 | 54.949 | 57.9105 | 6.7534 | OK
| 2015-11-19 02:00 | 19 | 1447.1755 | 38.9846 | 12.5996 | 2.6135 | 8.575 | 1.1263 | 20.8952 | 2.9437 | 54.6095 | 57.5532 | 6.7117 | OK
| 2015-11-19 03:00 | 19 | 1442.5819 | 39.2273 | 12.5976 | 2.6135 | 7.7875 | 1.1299 | 20.9584 | 2.953 | 54.7749 | 57.7279 | 7.4129 | OK
| 2015-11-19 04:00 | 19 | 1450.0902 | 39.9916 | 12.5899 | 2.6135 | 7.7875 | 1.1241 | 20.8371 | 2.9377 | 54.4577 | 57.3954 | 7.3702 | OK
1 | 2015-11-19 05:00 | 19 | 1439.2632 | 38.8733 | 12.5995 | 2.5242 | 8.575 | 1.1325 | 21.0099 | 2.8588 | 53.0341 | 55.8929 | 6.5181 | OK
| 2015-11-19 06:00 | 19 | 1433.6021 | 38.5041 | 12.6004 | 2.5242 | 8.575 | 1.137 | 21.0944 | 2.8701 | 53.2476 | 56.1177 | 6.5443 | OK
| 2015-11-19 07:00 | 19 | 982.6378 | 38.5041 | 12.6032 | 2.5242 | 8.575 | 1.6588 | 30.7821 | 4.1872 | 77.7016 | 81.8888 | 9.5497 | OK
| 2015-11-19 08:00 | 19 | 757.4118 | 38.6039 | 12.5805 | 2.3388 | 8.575 | 2.1521 | 39.8636 | 5.0332 | 93.2328 | 98.2661 | 11.4596 | OK
| 2015-11-19 09:00 | 19 | 767.3682 | 38.7433 | 12.5967 | 2.3388 | 8.575 | 2.1241 | 39.3971 | 4.9679 | 92.1418 | 97.1098 | 11.3248 | OK
| 2015-11-19 10:00 | 19 | 773.6112 | 40.6841 | 12.5889 | 2.655 | 7.7875 | 2.107 | 39.055 | 5.5941 | 103.6917 | 109.2858 | 14.0335 | OK
| 2015-11-19 11:00 | 19 | 770.6224 | 40.6841 | 12.5849 | 2.5449 | 7.7875 | 2.1152 | 39.194 | 5.3829 | 99.7448 | 105.1277 | 13.4996 | OK
| 2015-11-19 12:00 | 19 | 767.3798 | 40.6841 | 12.5898 | 2.5725 | 7.7875 | 2.1241 | 39.375 | 5.4643 | 101.2927 | 106.757 | 13.7088 | OK
| 2015-11-19 13:00 | 19 | 768.633 | 40.6841 | 12.5974 | 2.5725 | 7.7875 | 2.1206 | 39.3346 | 5.4554 | 101.1887 | 106.6441 | 13.6943 | OK
| 2015-11-19 14:00 | 19 | 751.2988 | 40.6841 | 12.5923 | 2.5725 | 7.7875 | 2.1696 | 40.2258 | 5.5813 | 103.4813 | 109.0626 | 14.0048 | OK
| 2015-11-19 15:00 | 19 | 751.9181 | 40.6841 | 12.5916 | 2.5725 | 7.7875 | 2.1678 | 40.1903 | 5.5767 | 103.3899 | 108.9666 | 13.9925 | OK
| 2015-11-19 16:00 | 19 | 773.383 | 40.6841 | 12.5915 | 2.4625 | 7.7875 | 2.1076 | 39.0746 | 5.19 | 96.2213 | 101.4114 | 13.0223 | OK
| 2015-11-19 17:00 | 19 | 940.0702 | 40.7167 | 12.5969 | 2.4625 | 7.7875 | 1.7339 | 32.1598 | 4.2698 | 79.1936 | 83.4633 | 10.7176 | OK
| 2015-11-19 18:00 | 19 | 1334.8389 | 40.9597 | 12.5912 | 2.4625 | 7.7875 | 1.2211 | 22.6385 | 3.007 | 55.7474 | 58.7544 | 7.5447 | OK
| 2015-11-19 19:00 | 19 | 1433.0009 | 40.9597 | 12.5927 | 2.4625 | 7.7875 | 1.1375 | 21.0903 | 2.801 | 51.9349 | 54.7359 | 7.0287 | OK
| 2015-11-19 20:00 | 19 | 1435.0083 | 40.9597 | 12.6032 | 2.4625 | 7.7875 | 1.1359 | 21.0783 | 2.7971 | 51.9055 | 54.7026 | 7.0244 | OK
| 2015-11-19 21:00 | 19 | 1435.2408 | 40.9597 | 12.6023 | 2.4625 | 7.7875 | 1.1357 | 21.0735 | 2.7967 | 51.8936 | 54.6902 | 7.0228 | OK
| 2015-11-19 22:00 | 19 | 1443.3948 | 40.8133 | 12.6074 | 2.3731 | 7.7875 | 1.1293 | 20.963 | 2.68 | 49.7482 | 52.4282 | 6.7323 | OK
| 2015-11-19 23:00 | 19 | 1447.2598 | 40.4227 | 12.5948 | 2.3731 | 7.7875 | 1.1263 | 20.8861 | 2.6728 | 49.5658 | 52.2386 | 6.708 | OK
| 2015-11-20 | 20 | 1440.9164 | 40.4227 | 12.5967 | 2.3731 | 7.7875 | 1.1312 | 20.9812 | 2.6846 | 49.7914 | 52.476 | 6.7385 | OK
| 2015-11-20 01:00 | 20 | 1443.5515 | 40.312 | 12.6052 | 2.3731 | 7.7875 | 1.1292 | 20.957 | 2.6797 | 49.7341 | 52.4137 | 6.7305 | OK
| 2015-11-20 02:00 | 20 | 1442.259 | 39.8008 | 12.6009 | 2.3731 | 7.7875 | 1.1302 | 20.9686 | 2.6821 | 49.7617 | 52.4437 | 6.7343 | OK
| 2015-11-20 03:00 | 20 | 1450.1215 | 39.8008 | 12.604 | 2.3731 | 7.7875 | 1.124 | 20.8601 | 2.6675 | 49.5041 | 52.1717 | 6.6994 | OK
| 2015-11-20 04:00 | 20 | 1437.7821 | 40.1793 | 12.6033 | 2.3731 | 7.7875 | 1.1337 | 21.0378 | 2.6904 | 49.9259 | 52.6163 | 6.7565 | OK
| 2015-11-20 05:00 | 20 | 1440.9382 | 40.2849 | 12.592 | 2.38 | 7.7875 | 1.1312 | 20.973 | 2.6923 | 49.9156 | 52.6079 | 6.7554 | OK
1 | 2015-11-20 06:00 | 20 | 1441.0569 | 39.0027 | 12.5994 | 2.2838 | 8.575 | 1.1311 | 20.9836 | 2.5832 | 47.9222 | 50.5054 | 5.8898 | OK
| 2015-11-20 07:00 | 20 | 1403.8686 | 38.8813 | 12.6072 | 2.2838 | 8.575 | 1.1611 | 21.5528 | 2.6517 | 49.2221 | 51.8737 | 6.0494 | OK
| 2015-11-20 08:00 | 20 | 1445.8973 | 40.1569 | 12.6243 | 2.2838 | 7.7875 | 1.1273 | 20.9547 | 2.5746 | 47.8561 | 50.4307 | 6.4759 | OK
| 2015-11-20 09:00 | 20 | 1446.3294 | 41.3696 | 12.5972 | 2.2838 | 7 | 1.127 | 20.9035 | 2.5738 | 47.7392 | 50.313 | 7.1876 | OK
| 2015-11-20 10:00 | 20 | 1450.426 | 41.3696 | 12.5936 | 2.2838 | 7 | 1.1238 | 20.8385 | 2.5665 | 47.5908 | 50.1573 | 7.1653 | OK
| 2015-11-20 11:00 | 20 | 1442.5826 | 41.6197 | 12.5993 | 2.2838 | 7 | 1.1299 | 20.9613 | 2.5805 | 47.8712 | 50.4517 | 7.2074 | OK
| 2015-11-20 12:00 | 20 | 1438.1997 | 43.2033 | 12.5928 | 2.2838 | 6.65 | 1.1334 | 21.0142 | 2.5884 | 47.9921 | 50.5804 | 7.6061 | OK
| 2015-11-20 13:00 | 20 | 1424.1481 | 43.2033 | 12.5995 | 2.3662 | 6.65 | 1.1445 | 21.2328 | 2.7082 | 50.2409 | 52.9491 | 7.9623 | OK
| 2015-11-20 14:00 | 20 | 1450.1507 | 43.2033 | 12.6053 | 2.3662 | 6.65 | 1.124 | 20.8618 | 2.6596 | 49.363 | 52.0226 | 7.823 | OK
| 2015-11-20 15:00 | 20 | 1433.4891 | 42.6267 | 12.5961 | 2.3662 | 7 | 1.1371 | 21.0888 | 2.6906 | 49.9001 | 52.5907 | 7.513 | OK
| 2015-11-20 16:00 | 20 | 1450.9102 | 40.7619 | 12.6079 | 2.3662 | 7.7875 | 1.1234 | 20.8551 | 2.6583 | 49.3471 | 52.0054 | 6.6781 | OK
| 2015-11-20 17:00 | 20 | 1443.5097 | 40.7619 | 12.6009 | 2.3662 | 7.7875 | 1.1292 | 20.9504 | 2.6719 | 49.5727 | 52.2446 | 6.7088 | OK
| 2015-11-20 18:00 | 20 | 1440.9613 | 40.7108 | 12.6004 | 2.3662 | 7.7875 | 1.1312 | 20.9867 | 2.6766 | 49.6584 | 52.3351 | 6.7204 | OK
| 2015-11-20 19:00 | 20 | 1447.0108 | 40.2037 | 12.6039 | 2.3662 | 7.7875 | 1.1265 | 20.9047 | 2.6654 | 49.4646 | 52.13 | 6.6941 | OK
| 2015-11-20 20:00 | 20 | 1448.4039 | 41.6561 | 12.6028 | 2.3662 | 7 | 1.1254 | 20.8828 | 2.6629 | 49.4127 | 52.0756 | 7.4394 | OK
| 2015-11-20 21:00 | 20 | 1437.8948 | 41.5384 | 12.5983 | 2.3522 | 7 | 1.1336 | 21.028 | 2.6664 | 49.4614 | 52.1278 | 7.4468 | OK
| 2015-11-20 22:00 | 20 | 1439.5536 | 40.2036 | 12.5951 | 2.3522 | 7.7875 | 1.1323 | 20.9984 | 2.6634 | 49.3918 | 52.0551 | 6.6844 | OK
| 2015-11-20 23:00 | 20 | 1440.1613 | 40.2036 | 12.5954 | 2.3522 | 7.7875 | 1.1318 | 20.99 | 2.6622 | 49.3722 | 52.0344 | 6.6818 | OK
| 2015-11-21 | 21 | 1440.0076 | 40.2036 | 12.598 | 2.1601 | 7.7875 | 1.1319 | 20.9965 | 2.4451 | 45.3543 | 47.7994 | 6.138 | OK
| 2015-11-21 01:00 | 21 | 1441.4435 | 40.1926 | 12.6064 | 2.1601 | 7.7875 | 1.1308 | 20.9896 | 2.4426 | 45.3392 | 47.7818 | 6.1357 | OK
| 2015-11-21 02:00 | 21 | 1447.3663 | 40.1935 | 12.5939 | 2.1601 | 7.7875 | 1.1262 | 20.8831 | 2.4327 | 45.1092 | 47.5418 | 6.1049 | OK
| 2015-11-21 03:00 | 21 | 1440.7328 | 41.4438 | 12.6028 | 2.1601 | 7 | 1.1314 | 20.9939 | 2.4439 | 45.3486 | 47.7924 | 6.8275 | OK
| 2015-11-21 04:00 | 21 | 1437.5241 | 41.6514 | 12.5993 | 2.1601 | 7 | 1.1339 | 21.0351 | 2.4493 | 45.4375 | 47.8868 | 6.841 | OK
| 2015-11-21 05:00 | 21 | 1448.2809 | 39.9595 | 12.6039 | 2.3453 | 7.7875 | 1.1255 | 20.8864 | 2.6396 | 48.9852 | 51.6248 | 6.6292 | OK
| 2015-11-21 06:00 | 21 | 1438.7425 | 39.8432 | 12.6104 | 2.3453 | 7.7875 | 1.1329 | 21.0357 | 2.6571 | 49.3354 | 51.9925 | 6.6764 | OK
| 2015-11-21 07:00 | 21 | 1372.6121 | 39.6475 | 12.6149 | 2.3453 | 7.7875 | 1.1875 | 22.0571 | 2.7851 | 51.7309 | 54.5161 | 7.0005 | OK
| 2015-11-21 08:00 | 21 | 1430.2295 | 40.7923 | 12.6035 | 2.0363 | 7.7875 | 1.1397 | 21.1493 | 2.3207 | 43.0658 | 45.3864 | 5.8281 | OK
| 2015-11-21 09:00 | 21 | 1434.174 | 41.7385 | 12.6014 | 2.2355 | 7 | 1.1365 | 21.0877 | 2.5408 | 47.142 | 49.6828 | 7.0975 | OK
| 2015-11-21 10:00 | 21 | 1432.425 | 42.8606 | 12.5994 | 2.2355 | 6.65 | 1.1379 | 21.11 | 2.5439 | 47.192 | 49.7359 | 7.4791 | OK
| 2015-11-21 11:00 | 21 | 1388.9337 | 42.8606 | 12.5916 | 2.2355 | 6.65 | 1.1736 | 21.7576 | 2.6235 | 48.6398 | 51.2633 | 7.7088 | OK
| 2015-11-21 12:00 | 21 | 1442.963 | 42.8606 | 12.6121 | 2.1669 | 6.65 | 1.1296 | 20.9769 | 2.4478 | 45.4556 | 47.9034 | 7.2035 | OK
| 2015-11-21 13:00 | 21 | 1443.7669 | 42.8606 | 12.6202 | 2.3114 | 6.65 | 1.129 | 20.9787 | 2.6096 | 48.4902 | 51.0998 | 7.6842 | OK
| 2015-11-21 14:00 | 21 | 1444.5846 | 42.8606 | 12.5995 | 2.3114 | 6.65 | 1.1284 | 20.9326 | 2.6081 | 48.3835 | 50.9916 | 7.6679 | OK
| 2015-11-21 15:00 | 21 | 1441.3396 | 42.8606 | 12.6242 | 2.3114 | 6.65 | 1.1309 | 21.0208 | 2.6139 | 48.5874 | 51.2014 | 7.6995 | OK
| 2015-11-21 16:00 | 21 | 1447.7364 | 42.8606 | 12.6122 | 2.3114 | 6.65 | 1.1259 | 20.9081 | 2.6024 | 48.3269 | 50.9293 | 7.6585 | OK
| 2015-11-21 17:00 | 21 | 1451.4831 | 41.7071 | 12.6153 | 2.3114 | 7 | 1.123 | 20.8591 | 2.5957 | 48.2138 | 50.8094 | 7.2585 | OK
| 2015-11-21 18:00 | 21 | 1450.4367 | 38.8327 | 12.6104 | 2.3114 | 8.575 | 1.1238 | 20.8661 | 2.5976 | 48.23 | 50.8275 | 5.9274 | OK
| 2015-11-21 19:00 | 21 | 1459.131 | 38.8327 | 12.6002 | 2.3114 | 8.575 | 1.1171 | 20.7249 | 2.5821 | 47.9036 | 50.4857 | 5.8875 | OK
| 2015-11-21 20:00 | 21 | 1456.1595 | 38.8327 | 12.6156 | 2.3114 | 8.575 | 1.1194 | 20.7927 | 2.5873 | 48.0603 | 50.6476 | 5.9064 | OK
| 2015-11-21 21:00 | 21 | 1449.3521 | 38.8327 | 12.6084 | 2.359 | 8.575 | 1.1246 | 20.8784 | 2.6531 | 49.2525 | 51.9055 | 6.0531 | OK
1 | 2015-11-21 22:00 | 21 | 1451.2067 | 37.2587 | 12.6067 | 2.359 | 9.3625 | 1.1232 | 20.8489 | 2.6497 | 49.183 | 51.8327 | 5.5362 | OK
| 2015-11-21 23:00 | 21 | 1447.2631 | 37.2215 | 12.6161 | 2.359 | 9.3625 | 1.1263 | 20.9213 | 2.6569 | 49.3538 | 52.0107 | 5.5552 | OK
| 2015-11-22 | 22 | 1438.8904 | 37.2215 | 12.6157 | 2.359 | 9.3625 | 1.1328 | 21.0425 | 2.6723 | 49.6396 | 52.3119 | 5.5874 | OK
| 2015-11-22 01:00 | 22 | 1442.3989 | 37.2215 | 12.6154 | 2.359 | 9.3625 | 1.1301 | 20.9907 | 2.6658 | 49.5175 | 52.1833 | 5.5737 | OK
| 2015-11-22 02:00 | 22 | 1448.0169 | 37.2215 | 12.6074 | 2.359 | 9.3625 | 1.1257 | 20.896 | 2.6555 | 49.2942 | 51.9497 | 5.5487 | OK
| 2015-11-22 03:00 | 22 | 1444.3373 | 37.2215 | 12.5993 | 2.359 | 9.3625 | 1.1285 | 20.9358 | 2.6623 | 49.3879 | 52.0502 | 5.5594 | OK
| 2015-11-22 04:00 | 22 | 1443.8292 | 39.89 | 12.6146 | 2.359 | 7.7875 | 1.1289 | 20.9686 | 2.6632 | 49.4653 | 52.1285 | 6.6939 | OK
| 2015-11-22 05:00 | 22 | 1461.0335 | 40.299 | 12.6146 | 2.3799 | 7.7875 | 1.1156 | 20.7216 | 2.6551 | 49.3152 | 51.9703 | 6.6736 | OK
| 2015-11-22 06:00 | 22 | 1438.8746 | 40.299 | 12.6093 | 2.3799 | 7.7875 | 1.1328 | 21.032 | 2.696 | 50.0537 | 52.7497 | 6.7736 | OK
| 2015-11-22 07:00 | 22 | 1454.5985 | 40.299 | 12.607 | 2.3799 | 7.7875 | 1.1206 | 20.8008 | 2.6669 | 49.5036 | 52.1705 | 6.6993 | OK
| 2015-11-22 08:00 | 22 | 1382.5967 | 40.299 | 12.6147 | 2.2974 | 7.7875 | 1.1789 | 21.8974 | 2.7085 | 50.3067 | 53.0151 | 6.8077 | OK
| 2015-11-22 09:00 | 22 | 1752.1655 | 40.299 | 12.6237 | 2.2564 | 7.7875 | 0.93028 | 17.2911 | 2.0991 | 39.0157 | 41.1147 | 5.2796 | OK
1 | 2015-11-22 10:00 | 22 | 1811.3716 | 40.299 | 12.6065 | 2.2564 | 7.7875 | 0.89987 | 16.7031 | 2.0305 | 37.6888 | 39.7193 | 5.1004 | OK
| 2015-11-22 11:00 | 22 | 1809.2291 | 40.299 | 12.6233 | 2.2564 | 7.7875 | 0.90094 | 16.7452 | 2.0329 | 37.7838 | 39.8166 | 5.1129 | OK
| 2015-11-22 12:00 | 22 | 1556.7782 | 39.2592 | 12.6038 | 2.2564 | 7.7875 | 1.047 | 19.4305 | 2.3625 | 43.843 | 46.2055 | 5.9333 | OK
| 2015-11-22 13:00 | 22 | 1438.3798 | 39.1754 | 12.6014 | 2.3938 | 8.575 | 1.1332 | 21.0259 | 2.7127 | 50.3319 | 53.0446 | 6.186 | OK
| 2015-11-22 14:00 | 22 | 1425.1518 | 39.1754 | 12.6033 | 2.3938 | 8.575 | 1.1437 | 21.2244 | 2.7379 | 50.807 | 53.5449 | 6.2443 | OK
| 2015-11-22 15:00 | 22 | 1439.2045 | 39.1754 | 12.6041 | 2.3938 | 8.575 | 1.1326 | 21.0184 | 2.7111 | 50.3138 | 53.025 | 6.1837 | OK
| 2015-11-22 16:00 | 22 | 1445.8141 | 39.1261 | 12.5969 | 2.3938 | 8.575 | 1.1274 | 20.9104 | 2.6988 | 50.0554 | 52.7541 | 6.1521 | OK
| 2015-11-22 17:00 | 22 | 1445.6761 | 38.5854 | 12.6015 | 2.3938 | 8.575 | 1.1275 | 20.92 | 2.699 | 50.0782 | 52.7772 | 6.1548 | OK
| 2015-11-22 18:00 | 22 | 1443.5546 | 38.5854 | 12.6015 | 2.3938 | 8.575 | 1.1292 | 20.9507 | 2.703 | 50.1519 | 52.8549 | 6.1638 | OK
| 2015-11-22 19:00 | 22 | 1442.184 | 38.511 | 12.6048 | 2.3938 | 8.575 | 1.1302 | 20.9762 | 2.7055 | 50.2127 | 52.9183 | 6.1712 | OK
| 2015-11-22 20:00 | 22 | 1446.743 | 38.3274 | 12.6113 | 2.3938 | 8.575 | 1.1267 | 20.9209 | 2.697 | 50.0804 | 52.7774 | 6.1548 | OK
| 2015-11-22 21:00 | 22 | 1448.945 | 38.3274 | 12.6041 | 2.407 | 8.575 | 1.125 | 20.8772 | 2.7077 | 50.2507 | 52.9584 | 6.1759 | OK
| 2015-11-22 22:00 | 22 | 1438.9732 | 38.3274 | 12.6081 | 2.407 | 8.575 | 1.1328 | 21.0284 | 2.7265 | 50.6146 | 53.3411 | 6.2205 | OK
| 2015-11-22 23:00 | 22 | 1444.1374 | 37.6155 | 12.6027 | 2.407 | 8.575 | 1.1287 | 20.9444 | 2.7167 | 50.4124 | 53.1291 | 6.1958 | OK
| 2015-11-23 | 23 | 1443.3025 | 37.5925 | 12.5993 | 2.407 | 8.575 | 1.1294 | 20.9508 | 2.7183 | 50.4279 | 53.1462 | 6.1978 | OK
| 2015-11-23 01:00 | 23 | 1440.7746 | 37.5925 | 12.6113 | 2.407 | 8.575 | 1.1313 | 21.0075 | 2.7231 | 50.5644 | 53.2874 | 6.2143 | OK
| 2015-11-23 02:00 | 23 | 1451.9016 | 37.5925 | 12.6093 | 2.407 | 8.575 | 1.1227 | 20.8433 | 2.7022 | 50.169 | 52.8712 | 6.1657 | OK
| 2015-11-23 03:00 | 23 | 1445.4364 | 37.8959 | 12.5924 | 2.407 | 8.575 | 1.1277 | 20.9084 | 2.7143 | 50.3257 | 53.04 | 6.1854 | OK
| 2015-11-23 04:00 | 23 | 1438.3532 | 39.5217 | 12.5973 | 2.407 | 7.7875 | 1.1332 | 21.0196 | 2.7277 | 50.5933 | 53.321 | 6.847 | OK
| 2015-11-23 05:00 | 23 | 1442.2948 | 39.5217 | 12.6055 | 2.3936 | 7.7875 | 1.1301 | 20.9758 | 2.7051 | 50.2073 | 52.9124 | 6.7945 | OK
| 2015-11-23 06:00 | 23 | 1458.0481 | 39.5217 | 12.5992 | 2.3936 | 7.7875 | 1.1179 | 20.7388 | 2.6759 | 49.64 | 52.3159 | 6.7179 | OK
| 2015-11-23 07:00 | 23 | 1424.9043 | 39.5217 | 12.598 | 2.3936 | 7.7875 | 1.1439 | 21.2191 | 2.7381 | 50.7896 | 53.5277 | 6.8735 | OK
| 2015-11-23 08:00 | 23 | 1453.8665 | 39.6207 | 12.6262 | 2.3936 | 7.7875 | 1.1211 | 20.843 | 2.6836 | 49.8894 | 52.573 | 6.7509 | OK
| 2015-11-23 09:00 | 23 | 1437.7223 | 40.1859 | 12.6051 | 2.3936 | 7.7875 | 1.1337 | 21.0418 | 2.7137 | 50.3653 | 53.079 | 6.8159 | OK
| 2015-11-23 10:00 | 23 | 1452.3259 | 40.1859 | 12.6204 | 2.3936 | 7.7875 | 1.1223 | 20.8555 | 2.6864 | 49.9195 | 52.6059 | 6.7552 | OK
| 2015-11-23 11:00 | 23 | 1443.4037 | 40.1859 | 12.6167 | 2.1533 | 7.7875 | 1.1293 | 20.9782 | 2.4317 | 45.1732 | 47.6049 | 6.113 | OK
| 2015-11-23 12:00 | 23 | 1442.6093 | 40.1859 | 12.5978 | 2.2975 | 7.7875 | 1.1299 | 20.9583 | 2.5959 | 48.1514 | 50.7474 | 6.5165 | OK
| 2015-11-23 13:00 | 23 | 1449.7165 | 40.1859 | 12.6059 | 2.2975 | 7.7875 | 1.1244 | 20.869 | 2.5832 | 47.9463 | 50.5295 | 6.4885 | OK
| 2015-11-23 14:00 | 23 | 1446.9082 | 40.1859 | 12.6079 | 2.1878 | 7.7875 | 1.1265 | 20.9128 | 2.4646 | 45.753 | 48.2176 | 6.1917 | OK
| 2015-11-23 15:00 | 23 | 1445.9037 | 39.4604 | 12.606 | 2.1878 | 7.7875 | 1.1273 | 20.9242 | 2.4664 | 45.7779 | 48.2443 | 6.1951 | OK
| 2015-11-23 16:00 | 23 | 1446.9384 | 39.0482 | 12.6066 | 2.1878 | 8.575 | 1.1265 | 20.9103 | 2.4646 | 45.7476 | 48.2121 | 5.6224 | OK
1 | 2015-11-23 17:00 | 23 | 1460.966 | 39.0482 | 12.6068 | 2.1878 | 8.575 | 1.1157 | 20.7098 | 2.4409 | 45.3089 | 47.7499 | 5.5685 | OK
| 2015-11-23 18:00 | 23 | 1435.5514 | 39.026 | 12.5979 | 2.1878 | 8.575 | 1.1355 | 21.0616 | 2.4841 | 46.0786 | 48.5628 | 5.6633 | OK
| 2015-11-23 19:00 | 23 | 1457.0063 | 38.8468 | 12.6108 | 2.1878 | 8.575 | 1.1187 | 20.7726 | 2.4476 | 45.4463 | 47.8939 | 5.5853 | OK
| 2015-11-23 20:00 | 23 | 1440.004 | 38.8593 | 12.6052 | 2.1878 | 8.575 | 1.1319 | 21.0086 | 2.4765 | 45.9627 | 48.4392 | 5.6489 | OK
| 2015-11-23 21:00 | 23 | 1440.8402 | 38.9422 | 12.6011 | 2.1878 | 8.575 | 1.1313 | 20.9896 | 2.475 | 45.921 | 48.396 | 5.6438 | OK
| 2015-11-23 22:00 | 23 | 1443.8082 | 38.9422 | 12.6167 | 2.4072 | 8.575 | 1.129 | 20.9723 | 2.7176 | 50.4841 | 53.2017 | 6.2043 | OK
| 2015-11-23 23:00 | 23 | 1439.9994 | 38.9422 | 12.6039 | 2.4072 | 8.575 | 1.1319 | 21.0064 | 2.7248 | 50.5662 | 53.291 | 6.2147 | OK
| 2015-11-24 | 24 | 1444.6664 | 38.9422 | 12.6111 | 2.4072 | 8.575 | 1.1283 | 20.9506 | 2.716 | 50.4319 | 53.1479 | 6.198 | OK
| 2015-11-24 01:00 | 24 | 1445.388 | 39.2399 | 12.5999 | 2.4072 | 7.7875 | 1.1277 | 20.9215 | 2.7146 | 50.3617 | 53.0764 | 6.8156 | OK
| 2015-11-24 02:00 | 24 | 1456.0661 | 39.7089 | 12.6122 | 2.4072 | 7.7875 | 1.1195 | 20.7884 | 2.6947 | 50.0413 | 52.7361 | 6.7719 | OK
| 2015-11-24 03:00 | 24 | 1440.2052 | 39.0347 | 12.599 | 2.4072 | 8.575 | 1.1318 | 20.9953 | 2.7244 | 50.5394 | 53.2638 | 6.2115 | OK
1 | 2015-11-24 04:00 | 24 | 1443.5964 | 38.5006 | 12.5993 | 2.4072 | 8.575 | 1.1291 | 20.9466 | 2.718 | 50.4221 | 53.1401 | 6.1971 | OK
| 2015-11-24 05:00 | 24 | 1446.0861 | 39.2671 | 12.6072 | 2.4072 | 7.7875 | 1.1272 | 20.9236 | 2.7133 | 50.3668 | 53.0801 | 6.8161 | OK
| 2015-11-24 06:00 | 24 | 1446.6336 | 39.7054 | 12.6055 | 2.3936 | 7.7875 | 1.1268 | 20.9129 | 2.697 | 50.0568 | 52.7538 | 6.7742 | OK
| 2015-11-24 07:00 | 24 | 1439.3424 | 39.7054 | 12.5927 | 2.3936 | 7.7875 | 1.1325 | 20.9975 | 2.7106 | 50.2593 | 52.9699 | 6.8019 | OK
| 2015-11-24 08:00 | 24 | 1440.4049 | 39.7054 | 12.5965 | 2.3936 | 7.7875 | 1.1316 | 20.9882 | 2.7086 | 50.2372 | 52.9458 | 6.7988 | OK
| 2015-11-24 09:00 | 24 | 1445.2391 | 39.7054 | 12.6002 | 2.3936 | 7.7875 | 1.1278 | 20.9243 | 2.6996 | 50.0841 | 52.7837 | 6.778 | OK
| 2015-11-24 10:00 | 24 | 1439.6524 | 39.7054 | 12.6002 | 2.3936 | 7.7875 | 1.1322 | 21.0054 | 2.7101 | 50.2782 | 52.9883 | 6.8043 | OK
| 2015-11-24 11:00 | 24 | 1449.8725 | 40.0091 | 12.5939 | 2.2151 | 7.7875 | 1.1242 | 20.8469 | 2.4903 | 46.1778 | 48.6681 | 6.2495 | OK
| 2015-11-24 12:00 | 24 | 1436.4363 | 40.0163 | 12.6031 | 2.3525 | 7.7875 | 1.1348 | 21.0573 | 2.6695 | 49.5372 | 52.2067 | 6.7039 | OK
| 2015-11-24 13:00 | 24 | 1444.35 | 40.0163 | 12.5952 | 2.4005 | 7.7875 | 1.1285 | 20.9287 | 2.7091 | 50.2403 | 52.9494 | 6.7993 | OK
| 2015-11-24 14:00 | 24 | 1436.6035 | 40.0163 | 12.5917 | 2.3455 | 7.7875 | 1.1346 | 21.0357 | 2.6613 | 49.3401 | 52.0013 | 6.6775 | OK
| 2015-11-24 15:00 | 24 | 1450.7828 | 40.0153 | 12.6061 | 2.3455 | 7.7875 | 1.1235 | 20.854 | 2.6353 | 48.9139 | 51.5492 | 6.6195 | OK
| 2015-11-24 16:00 | 24 | 1437.8946 | 39.4404 | 12.5965 | 2.3455 | 7.7875 | 1.1336 | 21.0249 | 2.6589 | 49.3147 | 51.9736 | 6.674 | OK
| 2015-11-24 17:00 | 24 | 1439.2625 | 39.4404 | 12.5912 | 2.3455 | 7.7875 | 1.1325 | 20.9961 | 2.6564 | 49.2472 | 51.9035 | 6.665 | OK
| 2015-11-24 18:00 | 24 | 1447.7064 | 39.4404 | 12.6147 | 2.3455 | 7.7875 | 1.1259 | 20.9126 | 2.6409 | 49.0512 | 51.6921 | 6.6378 | OK
| 2015-11-24 19:00 | 24 | 1438.9863 | 39.4404 | 12.5913 | 2.3455 | 7.7875 | 1.1327 | 21.0003 | 2.6569 | 49.2571 | 51.914 | 6.6663 | OK
| 2015-11-24 20:00 | 24 | 1455.7142 | 39.4404 | 12.6081 | 2.3112 | 7.7875 | 1.1197 | 20.7867 | 2.5879 | 48.042 | 50.6299 | 6.5014 | OK
| 2015-11-24 21:00 | 24 | 1441.0586 | 39.4404 | 12.596 | 2.3112 | 7.7875 | 1.1311 | 20.978 | 2.6142 | 48.484 | 51.0982 | 6.5616 | OK
| 2015-11-24 22:00 | 24 | 1444.5144 | 39.4404 | 12.6081 | 2.3112 | 7.7875 | 1.1284 | 20.9479 | 2.608 | 48.4145 | 51.0225 | 6.5518 | OK
| 2015-11-24 23:00 | 24 | 1439.1575 | 39.4646 | 12.589 | 2.3112 | 7.7875 | 1.1326 | 20.9939 | 2.6177 | 48.5207 | 51.1384 | 6.5667 | OK
| 2015-11-25 | 25 | 1451.888 | 39.8503 | 12.5992 | 2.3112 | 7.7875 | 1.1227 | 20.8267 | 2.5947 | 48.1344 | 50.7291 | 6.5142 | OK
| 2015-11-25 01:00 | 25 | 1438.688 | 39.8503 | 12.5938 | 2.3181 | 7.7875 | 1.133 | 21.0087 | 2.6264 | 48.7012 | 51.3276 | 6.591 | OK
| 2015-11-25 02:00 | 25 | 1441.605 | 39.8503 | 12.5944 | 2.3181 | 7.7875 | 1.1307 | 20.9673 | 2.6211 | 48.6051 | 51.2262 | 6.578 | OK
| 2015-11-25 03:00 | 25 | 1441.8374 | 39.8503 | 12.6038 | 2.3181 | 7.7875 | 1.1305 | 20.9795 | 2.6207 | 48.6335 | 51.2542 | 6.5816 | OK
| 2015-11-25 04:00 | 25 | 1438.0408 | 39.8503 | 12.5948 | 2.167 | 7.7875 | 1.1335 | 21.0199 | 2.4563 | 45.5509 | 48.0072 | 6.1646 | OK
| 2015-11-25 05:00 | 25 | 1442.4978 | 39.8503 | 12.6093 | 2.167 | 7.7875 | 1.13 | 20.9791 | 2.4487 | 45.4625 | 47.9112 | 6.1523 | OK
| 2015-11-25 06:00 | 25 | 1447.278 | 39.8503 | 12.599 | 2.167 | 7.7875 | 1.1263 | 20.8928 | 2.4406 | 45.2754 | 47.7161 | 6.1273 | OK
| 2015-11-25 07:00 | 25 | 1445.2926 | 39.8468 | 12.6066 | 2.167 | 7.7875 | 1.1278 | 20.934 | 2.444 | 45.3648 | 47.8087 | 6.1392 | OK
| 2015-11-25 08:00 | 25 | 1440.3005 | 39.8255 | 12.6089 | 2.167 | 7.7875 | 1.1317 | 21.0105 | 2.4525 | 45.5306 | 47.9831 | 6.1616 | OK
| 2015-11-25 09:00 | 25 | 1445.5068 | 39.8394 | 12.6101 | 2.167 | 7.7875 | 1.1276 | 20.9367 | 2.4436 | 45.3706 | 47.8142 | 6.1399 | OK
| 2015-11-25 10:00 | 25 | 1440.1411 | 39.9364 | 12.608 | 2.3868 | 7.7875 | 1.1318 | 21.0114 | 2.7015 | 50.1508 | 52.8523 | 6.7868 | OK
| 2015-11-25 11:00 | 25 | 1433.4262 | 39.928 | 12.6026 | 2.3868 | 7.7875 | 1.1371 | 21.1007 | 2.7142 | 50.3641 | 53.0782 | 6.8158 | OK
| 2015-11-25 12:00 | 25 | 1740.1979 | 39.928 | 12.6176 | 2.3868 | 7.7875 | 0.93668 | 17.4015 | 2.2357 | 41.5348 | 43.7705 | 5.6206 | OK
| 2015-11-25 13:00 | 25 | 1793.7966 | 39.928 | 12.6039 | 2.3868 | 7.7875 | 0.90869 | 16.8634 | 2.1689 | 40.2502 | 42.4191 | 5.4471 | OK
1 | 2015-11-25 14:00 | 25 | 1797.8032 | 39.928 | 12.6123 | 2.3868 | 7.7875 | 0.90666 | 16.8369 | 2.1641 | 40.187 | 42.3511 | 5.4383 | OK
| 2015-11-25 15:00 | 25 | 1556.8876 | 39.928 | 12.6104 | 2.3868 | 7.7875 | 1.047 | 19.4394 | 2.4989 | 46.3988 | 48.8977 | 6.279 | OK
| 2015-11-25 16:00 | 25 | 1454.9926 | 39.928 | 12.6207 | 2.2427 | 7.7875 | 1.1203 | 20.8178 | 2.5125 | 46.688 | 49.2004 | 6.3179 | OK
| 2015-11-25 17:00 | 25 | 1437.7965 | 39.4385 | 12.6039 | 2.2426 | 7.7875 | 1.1337 | 21.0388 | 2.5424 | 47.1813 | 49.7237 | 6.3851 | OK
| 2015-11-25 18:00 | 25 | 1452.2139 | 38.868 | 12.612 | 2.2426 | 8.575 | 1.1224 | 20.8433 | 2.5171 | 46.743 | 49.2601 | 5.7446 | OK
| 2015-11-25 19:00 | 25 | 1441.2699 | 38.868 | 12.6144 | 2.2426 | 8.575 | 1.1309 | 21.0054 | 2.5363 | 47.1065 | 49.6428 | 5.7892 | OK
| 2015-11-25 20:00 | 25 | 1440.6183 | 38.868 | 12.6085 | 2.2426 | 8.575 | 1.1315 | 21.0051 | 2.5374 | 47.1059 | 49.6433 | 5.7893 | OK
| 2015-11-25 21:00 | 25 | 1441.3566 | 38.868 | 12.6137 | 2.2426 | 8.575 | 1.1309 | 21.0031 | 2.5361 | 47.1014 | 49.6375 | 5.7886 | OK
| 2015-11-25 22:00 | 25 | 1440.2963 | 38.868 | 12.61 | 2.2426 | 8.575 | 1.1317 | 21.0123 | 2.538 | 47.1219 | 49.6599 | 5.7912 | OK
| 2015-11-25 23:00 | 25 | 1446.9091 | 38.868 | 12.6145 | 2.2426 | 8.575 | 1.1265 | 20.9238 | 2.5264 | 46.9236 | 49.45 | 5.7668 | OK
| 2015-11-26 | 26 | 1439.2824 | 38.868 | 12.6019 | 2.3868 | 8.575 | 1.1325 | 21.0136 | 2.7031 | 50.1563 | 52.8594 | 6.1644 | OK
| 2015-11-26 01:00 | 26 | 1460.472 | 39.1619 | 12.6149 | 2.3868 | 8.575 | 1.1161 | 20.7301 | 2.6639 | 49.4796 | 52.1435 | 6.0809 | OK
| 2015-11-26 02:00 | 26 | 1439.8344 | 39.3309 | 12.6038 | 2.3868 | 7.7875 | 1.1321 | 21.0088 | 2.7021 | 50.1448 | 52.8469 | 6.7861 | OK
| 2015-11-26 03:00 | 26 | 1453.4929 | 39.3309 | 12.6082 | 2.3868 | 7.7875 | 1.1214 | 20.8185 | 2.6767 | 49.6906 | 52.3673 | 6.7245 | OK
| 2015-11-26 04:00 | 26 | 1443.8715 | 39.3309 | 12.6055 | 2.3868 | 7.7875 | 1.1289 | 20.9528 | 2.6945 | 50.0111 | 52.7056 | 6.768 | OK
| 2015-11-26 05:00 | 26 | 1440.6157 | 39.3309 | 12.6036 | 2.3868 | 7.7875 | 1.1315 | 20.997 | 2.7006 | 50.1165 | 52.8171 | 6.7823 | OK
| 2015-11-26 06:00 | 26 | 1451.6354 | 39.3309 | 12.6002 | 2.3868 | 7.7875 | 1.1229 | 20.832 | 2.6801 | 49.7228 | 52.4029 | 6.7291 | OK
| 2015-11-26 07:00 | 26 | 1441.6207 | 39.605 | 12.5997 | 2.3868 | 7.7875 | 1.1307 | 20.9759 | 2.6987 | 50.0661 | 52.7648 | 6.7756 | OK
| 2015-11-26 08:00 | 26 | 1441.828 | 40.1647 | 12.6 | 2.2357 | 7.7875 | 1.1305 | 20.9734 | 2.5275 | 46.8911 | 49.4186 | 6.3459 | OK
| 2015-11-26 09:00 | 26 | 1435.8444 | 40.1647 | 12.597 | 2.2357 | 7.7875 | 1.1352 | 21.0557 | 2.5381 | 47.0752 | 49.6132 | 6.3709 | OK
| 2015-11-26 10:00 | 26 | 1443.1564 | 40.0933 | 12.6037 | 2.2357 | 7.7875 | 1.1295 | 20.9603 | 2.5252 | 46.8618 | 49.387 | 6.3418 | OK
| 2015-11-26 11:00 | 26 | 1439.8782 | 40.0905 | 12.6086 | 2.2357 | 7.7875 | 1.132 | 21.0162 | 2.5309 | 46.9867 | 49.5177 | 6.3586 | OK
| 2015-11-26 12:00 | 26 | 1446.1356 | 40.0905 | 12.6007 | 2.2769 | 7.7875 | 1.1271 | 20.912 | 2.5664 | 47.6155 | 50.1819 | 6.4439 | OK
| 2015-11-26 13:00 | 26 | 1441.0774 | 40.0905 | 12.5961 | 2.2769 | 7.7875 | 1.1311 | 20.9779 | 2.5754 | 47.7654 | 50.3408 | 6.4643 | OK
| 2015-11-26 14:00 | 26 | 1443.4176 | 40.0905 | 12.5947 | 2.2635 | 7.7875 | 1.1293 | 20.9414 | 2.556 | 47.4001 | 49.9561 | 6.4149 | OK
| 2015-11-26 15:00 | 26 | 1435.4265 | 39.6203 | 12.5917 | 2.2635 | 7.7875 | 1.1356 | 21.053 | 2.5703 | 47.6526 | 50.2229 | 6.4492 | OK
| 2015-11-26 16:00 | 26 | 1449.2166 | 38.2744 | 12.6056 | 2.2635 | 8.575 | 1.1247 | 20.8757 | 2.5458 | 47.2513 | 49.7971 | 5.8072 | OK
| 2015-11-26 17:00 | 26 | 1443.2569 | 38.2744 | 12.5921 | 2.2635 | 8.575 | 1.1294 | 20.9395 | 2.5563 | 47.3957 | 49.9521 | 5.8253 | OK
| 2015-11-26 18:00 | 26 | 1453.5689 | 38.2744 | 12.5923 | 2.2635 | 8.575 | 1.1214 | 20.7913 | 2.5382 | 47.0603 | 49.5985 | 5.7841 | OK
| 2015-11-26 19:00 | 26 | 1790.3859 | 38.2744 | 12.6057 | 2.2635 | 8.575 | 0.91042 | 16.8978 | 2.0607 | 38.2475 | 40.3082 | 4.7007 | OK
| 2015-11-26 20:00 | 26 | 1798.3712 | 38.2744 | 12.6083 | 2.2635 | 8.575 | 0.90638 | 16.8263 | 2.0515 | 38.0856 | 40.1371 | 4.6807 | OK
| 2015-11-26 21:00 | 26 | 1815.2303 | 38.2744 | 12.607 | 2.3866 | 8.575 | 0.89796 | 16.6683 | 2.1431 | 39.7809 | 41.924 | 4.8891 | OK
| 2015-11-26 22:00 | 26 | 1801.9447 | 38.2744 | 12.6128 | 2.2905 | 8.575 | 0.90458 | 16.7989 | 2.072 | 38.4784 | 40.5503 | 4.7289 | OK
1 | 2015-11-26 23:00 | 26 | 1803.6787 | 38.1642 | 12.5906 | 2.1877 | 8.575 | 0.90371 | 16.7533 | 1.977 | 36.651 | 38.628 | 4.5047 | OK
| 2015-11-27 | 27 | 1795.1963 | 37.9706 | 12.6077 | 2.1877 | 8.575 | 0.90798 | 16.8553 | 1.9864 | 36.8742 | 38.8606 | 4.5318 | OK
| 2015-11-27 01:00 | 27 | 1808.1792 | 37.9706 | 12.6165 | 2.3867 | 8.575 | 0.90146 | 16.7459 | 2.1515 | 39.9682 | 42.1197 | 4.9119 | OK
| 2015-11-27 02:00 | 27 | 1812.6076 | 37.9706 | 12.5963 | 2.3867 | 8.575 | 0.89926 | 16.6782 | 2.1463 | 39.8065 | 41.9528 | 4.8925 | OK
| 2015-11-27 03:00 | 27 | 1801.7472 | 37.9706 | 12.6135 | 2.3867 | 8.575 | 0.90468 | 16.8016 | 2.1592 | 40.1011 | 42.2603 | 4.9283 | OK
| 2015-11-27 04:00 | 27 | 1799.4622 | 37.9706 | 12.6061 | 2.3867 | 8.575 | 0.90583 | 16.8131 | 2.162 | 40.1285 | 42.2905 | 4.9318 | OK
| 2015-11-27 05:00 | 27 | 1812.0141 | 37.7578 | 12.6186 | 2.3867 | 8.575 | 0.89955 | 16.7133 | 2.147 | 39.8902 | 42.0372 | 4.9023 | OK
| 2015-11-27 06:00 | 27 | 1815.6233 | 37.5042 | 12.6077 | 2.3867 | 8.575 | 0.89776 | 16.6656 | 2.1427 | 39.7763 | 41.919 | 4.8885 | OK
| 2015-11-27 07:00 | 27 | 1808.2634 | 37.5704 | 12.6135 | 2.3867 | 8.575 | 0.90142 | 16.7412 | 2.1514 | 39.9569 | 42.1083 | 4.9106 | OK
| 2015-11-27 08:00 | 27 | 1808.883 | 37.6173 | 12.6175 | 2.3867 | 8.575 | 0.90111 | 16.7408 | 2.1507 | 39.9558 | 42.1065 | 4.9104 | OK
| 2015-11-27 09:00 | 27 | 1784.1432 | 37.5363 | 12.6147 | 2.3522 | 8.575 | 0.9136 | 16.9691 | 2.149 | 39.9142 | 42.0631 | 4.9053 | OK
| 2015-11-27 10:00 | 27 | 1810.8633 | 35.5645 | 12.6403 | 2.3522 | 10.15 | 0.90012 | 16.7526 | 2.1172 | 39.4051 | 41.5223 | 4.0909 | OK
1 | 2015-11-27 11:00 | 27 | 1823.0472 | 35.5645 | 12.62 | 2.3522 | 10.15 | 0.89411 | 16.6139 | 2.1031 | 39.0788 | 41.1819 | 4.0573 | OK
| 2015-11-27 12:00 | 27 | 1811.4271 | 35.5645 | 12.6201 | 2.3522 | 10.15 | 0.89984 | 16.7207 | 2.1166 | 39.33 | 41.4465 | 4.0834 | OK
| 2015-11-27 13:00 | 27 | 1812.6066 | 35.6212 | 12.6321 | 2.3522 | 9.3625 | 0.89926 | 16.7256 | 2.1152 | 39.3416 | 41.4568 | 4.428 | OK
| 2015-11-27 14:00 | 27 | 1805.8609 | 35.7022 | 12.6237 | 2.3522 | 9.3625 | 0.90262 | 16.777 | 2.1231 | 39.4625 | 41.5856 | 4.4417 | OK
| 2015-11-27 15:00 | 27 | 1800.4155 | 35.7022 | 12.6137 | 2.3522 | 9.3625 | 0.90535 | 16.8143 | 2.1295 | 39.5502 | 41.6798 | 4.4518 | OK
| 2015-11-27 16:00 | 27 | 1803.7146 | 35.7022 | 12.6182 | 2.3522 | 9.3625 | 0.90369 | 16.7896 | 2.1256 | 39.492 | 41.6177 | 4.4451 | OK
| 2015-11-27 17:00 | 27 | 1805.6546 | 35.7022 | 12.6274 | 2.3799 | 9.3625 | 0.90272 | 16.7838 | 2.1484 | 39.9436 | 42.092 | 4.4958 | OK
| 2015-11-27 18:00 | 27 | 1804.4878 | 35.7022 | 12.6193 | 2.3799 | 9.3625 | 0.9033 | 16.7838 | 2.1498 | 39.9437 | 42.0934 | 4.496 | OK
| 2015-11-27 19:00 | 27 | 1816.4538 | 35.7022 | 12.6241 | 2.3799 | 9.3625 | 0.89735 | 16.6796 | 2.1356 | 39.6956 | 41.8312 | 4.468 | OK
| 2015-11-27 20:00 | 27 | 1821.8261 | 35.7022 | 12.6256 | 2.3799 | 9.3625 | 0.89471 | 16.6325 | 2.1293 | 39.5834 | 41.7127 | 4.4553 | OK
| 2015-11-27 21:00 | 27 | 1798.3306 | 36.1021 | 12.6092 | 2.3799 | 9.3625 | 0.9064 | 16.8279 | 2.1571 | 40.0485 | 42.2056 | 4.5079 | OK
| 2015-11-27 22:00 | 27 | 1803.6217 | 36.5432 | 12.6317 | 2.3799 | 9.3625 | 0.90374 | 16.8084 | 2.1508 | 40.0021 | 42.1529 | 4.5023 | OK
| 2015-11-27 23:00 | 27 | 1802.1076 | 36.5432 | 12.6187 | 2.3799 | 9.3625 | 0.9045 | 16.8053 | 2.1526 | 39.9948 | 42.1474 | 4.5017 | OK
| 2015-11-28 | 28 | 1804.256 | 36.5432 | 12.6296 | 2.3799 | 9.3625 | 0.90342 | 16.7997 | 2.15 | 39.9814 | 42.1314 | 4.5 | OK
| 2015-11-28 01:00 | 28 | 1807.5428 | 36.5432 | 12.6191 | 2.3936 | 9.3625 | 0.90178 | 16.7552 | 2.1585 | 40.105 | 42.2635 | 4.5141 | OK
| 2015-11-28 02:00 | 28 | 1802.8551 | 36.5432 | 12.6212 | 2.2151 | 9.3625 | 0.90412 | 16.8017 | 2.0027 | 37.2172 | 39.2199 | 4.189 | OK
| 2015-11-28 03:00 | 28 | 1823.8351 | 36.5432 | 12.63 | 2.3867 | 9.3625 | 0.89372 | 16.62 | 2.1331 | 39.6675 | 41.8006 | 4.4647 | OK
| 2015-11-28 04:00 | 28 | 1812.4043 | 36.5432 | 12.6284 | 2.3867 | 9.3625 | 0.89936 | 16.7227 | 2.1465 | 39.9126 | 42.0591 | 4.4923 | OK
| 2015-11-28 05:00 | 28 | 1813.1193 | 36.5497 | 12.6237 | 2.3867 | 9.3625 | 0.899 | 16.7098 | 2.1457 | 39.8819 | 42.0276 | 4.4889 | OK
| 2015-11-28 06:00 | 28 | 1806.2703 | 36.5538 | 12.6217 | 2.3867 | 9.3625 | 0.90241 | 16.7705 | 2.1538 | 40.0267 | 42.1806 | 4.5053 | OK
| 2015-11-28 07:00 | 28 | 1710.9163 | 36.5538 | 12.6194 | 2.3867 | 9.3625 | 0.95271 | 17.7019 | 2.2739 | 42.2498 | 44.5237 | 4.7555 | OK
| 2015-11-28 08:00 | 28 | 1679.5797 | 36.5538 | 12.6209 | 2.3867 | 9.3625 | 0.97048 | 18.0344 | 2.3163 | 43.0434 | 45.3597 | 4.8448 | OK
| 2015-11-28 09:00 | 28 | 1828.6906 | 36.5538 | 12.6331 | 2.3662 | 9.3625 | 0.89135 | 16.5798 | 2.1091 | 39.231 | 41.3401 | 4.4155 | OK
| 2015-11-28 10:00 | 28 | 1798.5986 | 36.5538 | 12.6257 | 2.3662 | 9.3625 | 0.90626 | 16.8474 | 2.1444 | 39.8642 | 42.0086 | 4.4869 | OK
| 2015-11-28 11:00 | 28 | 1802.8698 | 36.5538 | 12.6258 | 2.3662 | 9.3625 | 0.90411 | 16.8076 | 2.1393 | 39.77 | 41.9093 | 4.4763 | OK
| 2015-11-28 12:00 | 28 | 1806.5293 | 36.5538 | 12.6384 | 2.3662 | 9.3625 | 0.90228 | 16.7903 | 2.135 | 39.7292 | 41.8641 | 4.4715 | OK
| 2015-11-28 13:00 | 28 | 1812.0618 | 35.6709 | 12.625 | 2.3662 | 9.3625 | 0.89953 | 16.7213 | 2.1285 | 39.5659 | 41.6943 | 4.4533 | OK
| 2015-11-28 14:00 | 28 | 1816.2618 | 35.2959 | 12.6251 | 2.3662 | 10.15 | 0.89745 | 16.6827 | 2.1235 | 39.4745 | 41.598 | 4.0983 | OK
| 2015-11-28 15:00 | 28 | 1817.9206 | 35.2959 | 12.6251 | 2.3662 | 10.15 | 0.89663 | 16.6675 | 2.1216 | 39.4386 | 41.5602 | 4.0946 | OK
1 | 2015-11-28 16:00 | 28 | 1807.4078 | 35.2959 | 12.6098 | 2.2975 | 10.15 | 0.90184 | 16.7441 | 2.072 | 38.4695 | 40.5415 | 3.9942 | OK
| 2015-11-28 17:00 | 28 | 1802.1596 | 35.2959 | 12.6139 | 2.2975 | 10.15 | 0.90447 | 16.7983 | 2.078 | 38.5939 | 40.6719 | 4.0071 | OK
| 2015-11-28 18:00 | 28 | 1802.4243 | 35.2959 | 12.6281 | 2.2975 | 10.15 | 0.90434 | 16.8148 | 2.0777 | 38.6318 | 40.7095 | 4.0108 | OK
| 2015-11-28 19:00 | 28 | 1794.0454 | 35.2959 | 12.6214 | 2.2975 | 10.15 | 0.90856 | 16.8843 | 2.0874 | 38.7916 | 40.879 | 4.0275 | OK
| 2015-11-28 20:00 | 28 | 1797.0056 | 35.2959 | 12.6265 | 2.2975 | 10.15 | 0.90706 | 16.8634 | 2.084 | 38.7435 | 40.8275 | 4.0224 | OK
| 2015-11-28 21:00 | 28 | 1812.1196 | 35.6702 | 12.6281 | 2.2975 | 9.3625 | 0.8995 | 16.7248 | 2.0666 | 38.425 | 40.4916 | 4.3249 | OK
| 2015-11-28 22:00 | 28 | 1821.4386 | 35.7552 | 12.6281 | 2.2975 | 9.3625 | 0.8949 | 16.6392 | 2.056 | 38.2285 | 40.2845 | 4.3027 | OK
| 2015-11-28 23:00 | 28 | 1815.2663 | 35.7552 | 12.6277 | 2.3112 | 9.3625 | 0.89794 | 16.6953 | 2.0753 | 38.5859 | 40.6612 | 4.343 | OK
| 2015-11-29 | 29 | 1803.7251 | 35.7552 | 12.6104 | 2.3112 | 9.3625 | 0.90369 | 16.7791 | 2.0886 | 38.7796 | 40.8682 | 4.3651 | OK
| 2015-11-29 01:00 | 29 | 1803.7731 | 35.7552 | 12.6266 | 2.0843 | 9.3625 | 0.90366 | 16.8002 | 1.8835 | 35.017 | 36.9005 | 3.9413 | OK
| 2015-11-29 02:00 | 29 | 1799.9255 | 36.1641 | 12.6198 | 2.0843 | 9.3625 | 0.90559 | 16.8271 | 1.8875 | 35.073 | 36.9606 | 3.9477 | OK
| 2015-11-29 03:00 | 29 | 1796.6758 | 36.6492 | 12.6285 | 2.3041 | 9.3625 | 0.90723 | 16.8692 | 2.0904 | 38.8687 | 40.959 | 4.3748 | OK
| 2015-11-29 04:00 | 29 | 1806.385 | 36.6492 | 12.631 | 2.3041 | 9.3625 | 0.90235 | 16.7818 | 2.0791 | 38.6674 | 40.7465 | 4.3521 | OK
| 2015-11-29 05:00 | 29 | 1804.821 | 36.6492 | 12.6235 | 2.3041 | 9.3625 | 0.90314 | 16.7864 | 2.0809 | 38.6779 | 40.7588 | 4.3534 | OK
| 2015-11-29 06:00 | 29 | 1818.5977 | 36.6492 | 12.6363 | 2.3041 | 9.3625 | 0.89629 | 16.6761 | 2.0652 | 38.4237 | 40.4889 | 4.3246 | OK
| 2015-11-29 07:00 | 29 | 1815.1394 | 36.6492 | 12.6033 | 2.3041 | 9.3625 | 0.898 | 16.6643 | 2.0691 | 38.3966 | 40.4657 | 4.3221 | OK
| 2015-11-29 08:00 | 29 | 1797.6141 | 36.6492 | 12.6075 | 2.3041 | 9.3625 | 0.90676 | 16.8323 | 2.0893 | 38.7838 | 40.8731 | 4.3656 | OK
| 2015-11-29 09:00 | 29 | 1804.6624 | 36.6492 | 12.6131 | 2.3041 | 9.3625 | 0.90322 | 16.774 | 2.0811 | 38.6493 | 40.7304 | 4.3504 | OK
| 2015-11-29 10:00 | 29 | 1810.6116 | 35.8247 | 12.6075 | 2.3041 | 9.3625 | 0.90025 | 16.7115 | 2.0743 | 38.5054 | 40.5797 | 4.3343 | OK
| 2015-11-29 11:00 | 29 | 1806.0199 | 35.1829 | 12.6152 | 2.2766 | 10.15 | 0.90254 | 16.7643 | 2.0547 | 38.1659 | 40.2206 | 3.9626 | OK
| 2015-11-29 12:00 | 29 | 1800.8896 | 35.1829 | 12.6077 | 2.2766 | 10.15 | 0.90511 | 16.802 | 2.0606 | 38.2517 | 40.3123 | 3.9717 | OK
| 2015-11-29 13:00 | 29 | 1800.1715 | 35.1829 | 12.61 | 2.2766 | 10.15 | 0.90547 | 16.8117 | 2.0614 | 38.2739 | 40.3353 | 3.9739 | OK
| 2015-11-29 14:00 | 29 | 1809.3611 | 35.1829 | 12.6051 | 2.2766 | 10.15 | 0.90087 | 16.7199 | 2.0509 | 38.0649 | 40.1158 | 3.9523 | OK
| 2015-11-29 15:00 | 29 | 1805.9534 | 35.1829 | 12.6185 | 2.2888 | 10.15 | 0.90257 | 16.7692 | 2.0658 | 38.3816 | 40.4474 | 3.985 | OK
| 2015-11-29 16:00 | 29 | 1809.7275 | 35.1829 | 12.6129 | 2.1394 | 10.15 | 0.90069 | 16.7267 | 1.927 | 35.7857 | 37.7126 | 3.7155 | OK
| 2015-11-29 17:00 | 29 | 1804.4988 | 35.1829 | 12.6152 | 2.1394 | 10.15 | 0.9033 | 16.7783 | 1.9325 | 35.896 | 37.8285 | 3.7269 | OK
1 | 2015-11-29 18:00 | 29 | 1813.1213 | 35.163 | 12.6144 | 2.1394 | 10.15 | 0.899 | 16.6975 | 1.9234 | 35.7232 | 37.6465 | 3.709 | OK
| 2015-11-29 19:00 | 29 | 1802.2956 | 35.1511 | 12.615 | 2.1394 | 10.15 | 0.9044 | 16.7986 | 1.9349 | 35.9393 | 37.8742 | 3.7315 | OK
| 2015-11-29 20:00 | 29 | 1808.3902 | 35.1511 | 12.6205 | 2.4142 | 10.15 | 0.90135 | 16.7493 | 2.1761 | 40.4368 | 42.6129 | 4.1983 | OK
| 2015-11-29 21:00 | 29 | 1800.5552 | 35.1511 | 12.6171 | 2.4142 | 10.15 | 0.90528 | 16.8176 | 2.1856 | 40.6018 | 42.7873 | 4.2155 | OK
| 2015-11-29 22:00 | 29 | 1805.8589 | 35.1511 | 12.6198 | 2.4142 | 10.15 | 0.90262 | 16.7718 | 2.1791 | 40.4913 | 42.6704 | 4.204 | OK
| 2015-11-29 23:00 | 29 | 1800.3572 | 35.2662 | 12.6287 | 2.4142 | 10.15 | 0.90538 | 16.8349 | 2.1858 | 40.6436 | 42.8294 | 4.2196 | OK
1 | 2015-11-30 | 30 | 1820.7954 | 35.568 | 12.6234 | 2.4142 | 10.15 | 0.89521 | 16.6389 | 2.1613 | 40.1704 | 42.3317 | 4.1706 | OK
| 2015-11-30 01:00 | 30 | 1804.7313 | 35.568 | 12.618 | 2.4142 | 10.15 | 0.90318 | 16.78 | 2.1805 | 40.5108 | 42.6913 | 4.206 | OK
| 2015-11-30 02:00 | 30 | 1814.2875 | 35.568 | 12.6262 | 2.4142 | 10.15 | 0.89842 | 16.7024 | 2.169 | 40.3236 | 42.4926 | 4.1865 | OK
| 2015-11-30 03:00 | 30 | 1812.0141 | 35.568 | 12.6238 | 2.4142 | 10.15 | 0.89955 | 16.7201 | 2.1717 | 40.3663 | 42.538 | 4.1909 | OK
| 2015-11-30 04:00 | 30 | 1794.7375 | 35.568 | 12.624 | 2.5379 | 10.15 | 0.90821 | 16.8814 | 2.305 | 42.844 | 45.149 | 4.4482 | OK
| 2015-11-30 05:00 | 30 | 1801.4268 | 35.568 | 12.6266 | 2.5379 | 10.15 | 0.90484 | 16.8221 | 2.2964 | 42.6935 | 44.99 | 4.4325 | OK
| 2015-11-30 06:00 | 30 | 1832.6168 | 35.568 | 12.6191 | 2.435 | 10.15 | 0.88944 | 16.526 | 2.1658 | 40.2408 | 42.4066 | 4.178 | OK
| 2015-11-30 07:00 | 30 | 1722.2323 | 35.9183 | 12.6082 | 2.5873 | 9.3625 | 0.94645 | 17.57 | 2.4487 | 45.4584 | 47.9072 | 5.1169 | OK
| 2015-11-30 08:00 | 30 | 1756.02 | 36.5078 | 12.6166 | 2.5873 | 9.3625 | 0.92824 | 17.2435 | 2.4016 | 44.6137 | 47.0153 | 5.0217 | OK
| 2015-11-30 09:00 | 30 | 1813.771 | 36.5078 | 12.6281 | 2.5873 | 9.3625 | 0.89868 | 16.7096 | 2.3251 | 43.2324 | 45.5575 | 4.866 | OK
| 2015-11-30 10:00 | 30 | 1795.3228 | 36.5078 | 12.6074 | 2.5516 | 9.3625 | 0.90791 | 16.8536 | 2.3167 | 43.0044 | 45.3211 | 4.8407 | OK
| 2015-11-30 11:00 | 30 | 1822.8207 | 36.5078 | 12.5999 | 2.3731 | 9.3625 | 0.89422 | 16.5896 | 2.1221 | 39.3696 | 41.4917 | 4.4317 | OK
| 2015-11-30 12:00 | 30 | 1802.8589 | 36.5078 | 12.605 | 2.5175 | 9.3625 | 0.90412 | 16.7801 | 2.2761 | 42.2439 | 44.52 | 4.7551 | OK
| 2015-11-30 13:00 | 30 | 1789.5948 | 35.9857 | 12.5927 | 2.5175 | 9.3625 | 0.91082 | 16.8879 | 2.293 | 42.5153 | 44.8083 | 4.7859 | OK
| 2015-11-30 14:00 | 30 | 1809.6691 | 35.7517 | 12.6077 | 2.5175 | 9.3625 | 0.90072 | 16.7205 | 2.2676 | 42.094 | 44.3615 | 4.7382 | OK
| 2015-11-30 15:00 | 30 | 1810.5858 | 35.7517 | 12.6007 | 2.5175 | 9.3625 | 0.90026 | 16.7027 | 2.2664 | 42.0491 | 44.3155 | 4.7333 | OK
| 2015-11-30 16:00 | 30 | 1804.9848 | 36.3227 | 12.6096 | 2.5175 | 9.3625 | 0.90305 | 16.7664 | 2.2734 | 42.2095 | 44.4829 | 4.7512 | OK
| 2015-11-30 17:00 | 30 | 1800.5384 | 36.4548 | 12.6039 | 2.5724 | 9.3625 | 0.90528 | 16.8002 | 2.3288 | 43.2169 | 45.5457 | 4.8647 | OK
| 2015-11-30 18:00 | 30 | 1804.0496 | 36.4548 | 12.609 | 2.5724 | 9.3625 | 0.90352 | 16.7742 | 2.3242 | 43.1501 | 45.4743 | 4.8571 | OK
| 2015-11-30 19:00 | 30 | 1819.1567 | 36.4548 | 12.611 | 2.5724 | 9.3625 | 0.89602 | 16.6377 | 2.3049 | 42.7988 | 45.1037 | 4.8175 | OK
| 2015-11-30 20:00 | 30 | 1807.1384 | 36.4649 | 12.5981 | 2.5861 | 9.3625 | 0.90198 | 16.7311 | 2.3326 | 43.2683 | 45.6009 | 4.8706 | OK
| 2015-11-30 21:00 | 30 | 1802.2588 | 36.4654 | 12.6181 | 2.3591 | 9.3625 | 0.90442 | 16.8031 | 2.1336 | 39.6406 | 41.7743 | 4.4619 | OK
| 2015-11-30 22:00 | 30 | 1801.5253 | 36.4654 | 12.6122 | 2.593 | 9.3625 | 0.90479 | 16.802 | 2.3461 | 43.5668 | 45.9128 | 4.9039 | OK
| 2015-11-30 23:00 | 30 | 1812.313 | 36.4654 | 12.6178 | 2.593 | 9.3625 | 0.8994 | 16.7094 | 2.3321 | 43.3267 | 45.6588 | 4.8768 | OK
|  | #VALUE! | 1816.1229 | 36.4654 | 12.6061 | 2.593 | 9.3625 | 0.89752 | 16.6589 | 2.3272 | 43.1957 | 45.523 | 4.8623 | OK
| #VALUE! | #VALUE! | 1796.4106 | 36.4654 | 12.6036 | 2.593 | 9.3625 | 0.90736 | 16.8384 | 2.3528 | 43.6611 | 46.0139 | 4.9147 | OK
| #VALUE! | #VALUE! | 1808.5125 | 36.4654 | 12.6149 | 2.6065 | 9.3625 | 0.90129 | 16.7407 | 2.3493 | 43.6353 | 45.9846 | 4.9116 | OK
| #VALUE! | #VALUE! | 1811.2552 | 36.4664 | 12.6066 | 2.6065 | 9.3625 | 0.89993 | 16.7043 | 2.3457 | 43.5405 | 45.8862 | 4.9011 | OK
| #VALUE! | #VALUE! | 1810.0358 | 36.5078 | 12.6179 | 2.6065 | 9.3625 | 0.90053 | 16.7306 | 2.3473 | 43.6091 | 45.9564 | 4.9086 | OK
| #VALUE! | #VALUE! | 1801.1971 | 36.5078 | 12.6149 | 2.6065 | 9.3625 | 0.90495 | 16.8087 | 2.3588 | 43.8127 | 46.1715 | 4.9315 | OK
| #VALUE! | #VALUE! | 1799.9643 | 36.5078 | 12.6115 | 2.6065 | 9.3625 | 0.90557 | 16.8156 | 2.3604 | 43.8307 | 46.1911 | 4.9336 | OK
| #VALUE! | #VALUE! | 1812.8808 | 36.5923 | 12.6063 | 2.6065 | 9.3625 | 0.89912 | 16.689 | 2.3436 | 43.5006 | 45.8442 | 4.8966 | OK
| #VALUE! | #VALUE! | 1815.5345 | 36.7516 | 12.6048 | 2.6065 | 9.3625 | 0.89781 | 16.6627 | 2.3402 | 43.4319 | 45.7721 | 4.8889 | OK
| #VALUE! | #VALUE! | 1820.0652 | 36.7516 | 12.6078 | 2.6065 | 9.3625 | 0.89557 | 16.6251 | 2.3343 | 43.334 | 45.6683 | 4.8778 | OK
| #VALUE! | #VALUE! | 1806.1867 | 36.7516 | 12.6194 | 2.5034 | 9.3625 | 0.90245 | 16.7682 | 2.2592 | 41.9772 | 44.2364 | 4.7249 | OK
| #VALUE! | #VALUE! | 1781.696 | 35.6577 | 12.6212 | 2.5034 | 9.3625 | 0.91486 | 17.0011 | 2.2902 | 42.5602 | 44.8505 | 4.7904 | OK
| #VALUE! | #VALUE! | 1801.8418 | 34.985 | 12.6202 | 2.5034 | 10.15 | 0.90463 | 16.8098 | 2.2646 | 42.0813 | 44.3459 | 4.3691 | OK
| #VALUE! | #VALUE! | 1817.4516 | 35.2141 | 12.6199 | 2.5034 | 10.15 | 0.89686 | 16.665 | 2.2452 | 41.7189 | 43.964 | 4.3314 | OK
| #VALUE! | #VALUE! | 1798.2564 | 35.3631 | 12.6256 | 2.537 | 10.15 | 0.90643 | 16.8505 | 2.2996 | 42.7493 | 45.0489 | 4.4383 | OK
| #VALUE! | #VALUE! | 1793.1169 | 35.9957 | 12.6255 | 2.537 | 9.3625 | 0.90903 | 16.8987 | 2.3062 | 42.8716 | 45.1778 | 4.8254 | OK
| #VALUE! | #VALUE! | 1672.3014 | 36.1686 | 12.6282 | 1.5829 | 9.3625 | 0.9747 | 18.1233 | 1.5428 | 28.6866 | 30.2294 | 3.2288 | OK
| #VALUE! | #VALUE! | 356.4086 | 35.9548 | 12.866 | 1.0671 | 9.3625 | 4.5734 | 86.6378 | 4.88 | 92.4469 | 97.3269 | 10.3954 | OK
1 | #VALUE! | #VALUE! | 1259.3926 | 35.7446 | 12.6882 | 1.1083 | 9.3625 | 1.2943 | 24.1796 | 1.4344 | 26.797 | 28.2314 | 3.0154 | OK
| #VALUE! | #VALUE! | 1797.9811 | 35.7446 | 12.6075 | 2.3042 | 9.3625 | 0.90657 | 16.8289 | 2.089 | 38.7777 | 40.8667 | 4.3649 | OK
| #VALUE! | #VALUE! | 1795.9318 | 35.7446 | 12.6197 | 2.3042 | 9.3625 | 0.90761 | 16.8644 | 2.0913 | 38.8595 | 40.9509 | 4.3739 | OK
| #VALUE! | #VALUE! | 1797.0085 | 35.7446 | 12.6214 | 2.5515 | 9.3625 | 0.90706 | 16.8565 | 2.3144 | 43.0101 | 45.3245 | 4.8411 | OK
| #VALUE! | #VALUE! | 1795.3462 | 35.7446 | 12.629 | 2.5515 | 9.3625 | 0.9079 | 16.8823 | 2.3165 | 43.0759 | 45.3924 | 4.8483 | OK
| #VALUE! | #VALUE! | 1802.5911 | 36.1707 | 12.6279 | 2.5515 | 9.3625 | 0.90425 | 16.813 | 2.3072 | 42.899 | 45.2063 | 4.8284 | OK
NOTES, CALCULATIONS, AND ASSUMPTIONS
Quinns must obtain 3.5 log removal credit for virus from chlorine disinfection prior to the first customer.
Yellow fields are for input.
Compliance ration must be greater than 1.0 ninety-five percent of the time on a monthly basis.
Required CTr for 3.5 log removal taken from Table C-7, EPA Guidance Manual Disinfection Profiling and Benchmarking and interpolated
Sequence 1 Inlet Pipe time = (Clearwell inlet pipe volume) / (flow in gpm) * (T10/T ratio)
Sequence 2 Clearwell time = (Clearwell volume/ft depth) * depth / (flow in gpm) * (T10/T ratio)
CTa = (time) * (chlorine concentration)
Total Cta = Clearwell Cta + Clearwell Inlet Cta
Contact volume per ft of clearwell includes the volume from the inlet up to the first pump (the way the water flows).
The clearwell inlet pipe volume is 1,630 gallons based on 100 ft of 20" pipe
132000
[6 empty] | Volume | T10/T
[6 empty] | (Gals) | (-)
| Sequence 1: Clearwell inlet pipe |  |  |  |  | 1630 | 1 | 100 ft of 20" pipe
| Sequence 2: Clearwell Contact Vol per ft depth |  |  |  |  | 8000 | 0.3 | Contact volume includes the 70.5' of the north leg, and 42 ft of the south leg
Required CTr for 3.5 log removal taken from Table C-7, EPA Guidance Manual Disinfection Profiling and Benchmarking and interpolated
| Temp (Deg F) |  | 32.9 | 33.8 | 35.6 | 37.4 | 39.2 | 41 | 42.8 | 43.8 | 46.4 | 48.2 | 50 | 51.8
| Temp (Deg C) |  | 0.5 | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11
| Req'd CTr (mg-min/L) |  | 10.5 | 10.15 | 9.3625 | 8.575 | 7.7875 | 7 | 6.65 | 6.3 | 5.95 | 5.6 | 5.25 | 4.9
Formulas:
Date and Time = [Date and Time, row above]+1/24
Date and Time = '[1]Turbidity Daily Data Sheet'!B17

## Disinfection Report
Monthly Report for Water Treatment Technique Compliance - Disinfection
| Month: | 2015-11-01 |  |  | Utility Name: | Park City Water
| Year: | 2015-11-01 |  |  | Treatment Plant: | Quinn's Junction
| System Number: | 22011 |  |  | Filtration Technology: | Membrane Filtration
Prepared by:
D. | Record the daily minimum disinfectant residual at the point-of-entry (POE) to the distribution system
and the minimum daily plant total inactivation ratio (CTprovided/CTrequired).
|  | Min POE |  |  |  | Min POE
|  | Cl2 Res | Total Inactivation |  |  | Cl2 Res | Total Inactivation
| Date | (mg/L) | Ratio |  | Date | (mg/L) | Ratio
| 2015-11-01 | 2.2286 | 10.7996 |  | 2015-11-16 | 2.4074 | 6.6959
| 2015-11-02 | 2.2904 | 7.9754 |  | 2015-11-17 | 2.4625 | 6.3716
| 2015-11-03 | 2.0158 | 11.4402 |  | 2015-11-18 | 2.6069 | 6.4139
| 2015-11-04 | 2.2287 | 11.1329 |  | 2015-11-19 | 2.3731 | 6.5181
| 2015-11-05 | 2.2493 | 9.9118 |  | 2015-11-20 | 2.3522 | 5.8898
| 2015-11-06 | 2.2835 | 8.0802 |  | 2015-11-21 | 2.1669 | 5.5362
| 2015-11-07 | 2.304 | 7.6757 |  | 2015-11-22 | 2.359 | 5.1004
| 2015-11-08 | 2.0639 | 6.9586 |  | 2015-11-23 | 2.1878 | 5.5685
| 2015-11-09 | 2.2356 | 7.7266 |  | 2015-11-24 | 2.373 | 6.1971
| 2015-11-10 | 2.2015 | 7.1637 |  | 2015-11-25 | 2.2427 | 5.4383
| 2015-11-11 | 2.4898 | 6.4076 |  | 2015-11-26 | 2.2358 | 4.5047
| 2015-11-12 | 2.5103 | 6.0785 |  | 2015-11-27 | 2.3522 | 4.0573
| 2015-11-13 | 2.4833 | 5.8378 |  | 2015-11-28 | 2.2975 | 3.9942
| 2015-11-14 | 2.2217 | 5.4365 |  | 2015-11-29 | 2.0843 | 3.709
| 2015-11-15 | 2.3591 | 6.7471 |  | 2015-11-30 | 2.4966 | 4.1706
E. | Record the date of occurrence, duration and date reported for each time the disinfectant residual
was less than 0.2 mg/L or the total Inactivation Ratio was less than 1. Attach details of public
notice for each event. If none, enter "none".
|  | Type of Event |  | Pertinent Residual or
| Date | (Residual or Total | Duration | Total Inactivation |  | Date Reported | Date of Public
|  | Inactivation) | (Hours) | Ratio Value |  | to State | Notice
none
none
none
none
F. | Distribution System Disinfectant Residual Criteria
[6 empty] | Number of sites where disinfectant residual measurements were made | A =
[6 empty] | Number of sites where HPC samples were taken instead of residual measurements | B =
[6 empty] | Number of sites where no residual was detected and no HPC sample was taken | C =
[6 empty] | Number of sites where no residual was detected and HPC exceeded 500 | D =
[6 empty] | Number of sites where no residual measurement was made and HPC exceeded 500 | E =
| Violation percentage for this month* |  |  | #DIV/0! | Violation percentage for last month* |  |  | 0
Violation percentage = 100x(C+D+E)/(A+B)
Formulas:
Month: = [Month:, row above]+1
Utility Name: = [Utility Name:, row above]+1
Utility Name: = IF('EPA Monthly Summary'!F5<>2,[Utility Name:, row above]+1,"")

## Sequence 1
FIRST DISINFECTION SEQUENCE -- INLET PIPE - Quinns WTP
| Month: | 2015-11-01 |  |  | Utility Name: | Park City Municipal Corporation
| Year: | 2012-06-01 |  |  | Treatment Plant: | Quinn's WTP
| System Number: | 22011 |  |  | Prepared by:
[7 empty] | Giardia and Crypto Log Inactivation Treatment Credit granted by Utah DDW: | 4
[7 empty] | Required Giardia and Crypto Log Inactivation for Disinfection: | None
[7 empty] | Virus Log Inactivation Treatment Credit granted by Utah DDW: | 0.5
[7 empty] | Required Virus Log Inactivation for Disinfection (see table below): | 3.5
Inactivation Ratio Calculation - All data for the same point in time, and at the end of the sequence.
|  | Peak Flow | Peak Flow Cl2 |  |  |  | CT Required | Inactivation
| Date | Detention Time | Residual |  | Temperature | CT Provided | 3.5 log Virus | Ratio
|  | (Minutes) | (mg/l) | pH | (Deg C) | (min.*mg/L) | (min.*mg/L) | Provided
| 1 | 0.53925 | 2.1462 |  | 9.0981 | 1.1573 | 5.6 | 0.20666
| 2 | 1.1567 | 1.9745 |  | 9.4803 | 2.2839 | 5.6 | 0.40784
| 3 | 1.5238 | 2.2835 |  | 8.582 | 3.4796 | 5.95 | 0.58481
| 4 | 1.5295 | 2.3453 |  | 7.8847 | 3.5871 | 6.3 | 0.56938
| 5 | 1.5166 | 2.105 |  | 7.7944 | 3.1925 | 6.3 | 0.50674
| 6 | 1.1197 | 2.3249 |  | 27.4183 | 2.6031 | 6.3 | 0.41319
| 7 | 1.2883 | 2.1324 |  | 5.0444 | 2.7471 | 7 | 0.39244
| 8 | 1.2986 | 2.1324 |  | 4.7676 | 2.769 | 7.7875 | 0.35557
| 9 | 1.2035 | 2.2974 |  | 5.0875 | 2.7649 | 7 | 0.39499
| 10 | 0.95471 | 2.5516 |  | 6.2044 | 2.4361 | 6.65 | 0.36633
| 11 | 1.0251 | 2.4898 |  | 4.4417 | 2.5522 | 7.7875 | 0.32773
| 12 | 1.0263 | 2.359 |  | 4.4445 | 2.4211 | 7.7875 | 0.31089
| 13 | 1.1278 | 2.2699 |  | 3.8862 | 2.5601 | 8.575 | 0.29855
| 14 | 0.90201 | 2.4006 |  | 4.2101 | 2.1654 | 7.7875 | 0.27806
| 15 | 1.1254 | 2.3866 |  | 4.8873 | 2.6859 | 7.7875 | 0.3449
| 16 | 1.1236 | 2.3729 |  | 4.4673 | 2.6662 | 7.7875 | 0.34237
| 17 | 1.1287 | 2.4762 |  | 3.9333 | 2.795 | 8.575 | 0.32595
| 18 | 0.95033 | 2.6894 |  | 4.585 | 2.5558 | 7.7875 | 0.32819
| 19 | 1.1325 | 2.5242 |  | 3.8185 | 2.8588 | 8.575 | 0.33338
| 20 | 1.1311 | 2.2838 |  | 3.8904 | 2.5832 | 8.575 | 0.30125
| 21 | 1.1232 | 2.359 |  | 2.9215 | 2.6497 | 9.3625 | 0.28301
| 22 | 0.89987 | 2.2564 |  | 4.6106 | 2.0305 | 7.7875 | 0.26073
| 23 | 1.1157 | 2.1878 |  | 3.9157 | 2.4409 | 8.575 | 0.28466
| 24 | 1.1291 | 2.4072 |  | 3.6114 | 2.718 | 8.575 | 0.31697
| 25 | 0.90666 | 2.3868 |  | 4.4044 | 2.1641 | 7.7875 | 0.27789
| 26 | 0.90371 | 2.1877 |  | 3.4245 | 1.977 | 8.575 | 0.23056
| 27 | 0.89411 | 2.3522 |  | 1.9803 | 2.1031 | 10.15 | 0.2072
| 28 | 0.90184 | 2.2975 |  | 1.8311 | 2.072 | 10.15 | 0.20414
| 31 | 0.899 | 2.1394 |  | 1.7572 | 1.9234 | 10.15 | 0.18949
| 31 | 0.89521 | 2.4142 |  | 1.9822 | 2.1613 | 10.15 | 0.21293
| AVG | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | 0 | 0 | 0
| MAX | 0 | 0 | 0 | 0 | 0 | 0 | 0
| MIN | 0 | 0 | 0 | 0 | 0 | 0 | 0

## Sequence 2
SECOND DISINFECTION SEQUENCE - CLEARWELL - Quinns WTP
| Month: | 2015-11-01 |  |  | Utility Name: | Park City Municipal Corporation
| Year: | 2012-06-01 |  |  | Treatment Plant: | Quinn's WTP
| System Number: | 22011 |  |  | Prepared by:
[7 empty] | Giardia and Crypto Log Inactivation Treatment Credit granted by Utah DDW: | 4
[7 empty] | Required Giardia and Crypto Log Inactivation for Disinfection: | None
[7 empty] | Virus Log Inactivation Treatment Credit granted by Utah DDW: | 0.5
[7 empty] | Required Virus Log Inactivation for Disinfection (see table below): | 3.5
Inactivation Ratio Calculation - All data for the same point in time, and at the end of the sequence.
|  | Peak Flow | Peak Flow Cl2 |  |  |  | CT Required | Inactivation
| Date | Detention Time | Residual |  | Temperature | CT Provided | 3.5 log Virus | Ratio
|  | (Minutes) | (mg/l) | pH | (Deg C) | (min.*mg/L) | (min.*mg/L) | Provided
| 1 | 27.6402 | 2.1462 |  | 9.0981 | 59.3207 | 5.6 | 10.593
| 2 | 21.4625 | 1.9745 |  | 9.4803 | 42.3782 | 5.6 | 7.5675
| 3 | 28.2856 | 2.2835 |  | 8.582 | 64.5894 | 5.95 | 10.8554
| 4 | 28.3756 | 2.3453 |  | 7.8847 | 66.5501 | 6.3 | 10.5635
| 5 | 28.1485 | 2.105 |  | 7.7944 | 59.2518 | 6.3 | 9.4051
| 6 | 20.7763 | 2.3249 |  | 27.4183 | 48.3024 | 6.3 | 7.6671
| 7 | 23.9092 | 2.1324 |  | 5.0444 | 50.9831 | 7 | 7.2833
| 8 | 24.1147 | 2.1324 |  | 4.7676 | 51.4213 | 7.7875 | 6.6031
| 9 | 22.339 | 2.2974 |  | 5.0875 | 51.3213 | 7 | 7.3316
| 10 | 17.715 | 2.5516 |  | 6.2044 | 45.2024 | 6.65 | 6.7974
| 11 | 19.0163 | 2.4898 |  | 4.4417 | 47.3466 | 7.7875 | 6.0798
| 12 | 19.0397 | 2.359 |  | 4.4445 | 44.915 | 7.7875 | 5.7676
| 13 | 20.9257 | 2.2699 |  | 3.8862 | 47.4988 | 8.575 | 5.5392
| 14 | 16.7336 | 2.4006 |  | 4.2101 | 40.1715 | 7.7875 | 5.1585
| 15 | 20.8903 | 2.3866 |  | 4.8873 | 49.8574 | 7.7875 | 6.4022
| 16 | 20.8511 | 2.3729 |  | 4.4673 | 49.4783 | 7.7875 | 6.3536
| 17 | 20.9358 | 2.4762 |  | 3.9333 | 51.8413 | 8.575 | 6.0456
| 18 | 17.622 | 2.6894 |  | 4.585 | 47.3922 | 7.7875 | 6.0857
| 19 | 21.0099 | 2.5242 |  | 3.8185 | 53.0341 | 8.575 | 6.1847
| 20 | 20.9836 | 2.2838 |  | 3.8904 | 47.9222 | 8.575 | 5.5886
| 21 | 20.8489 | 2.359 |  | 2.9215 | 49.183 | 9.3625 | 5.2532
| 22 | 16.7031 | 2.2564 |  | 4.6106 | 37.6888 | 7.7875 | 4.8397
| 23 | 20.7098 | 2.1878 |  | 3.9157 | 45.3089 | 8.575 | 5.2838
| 24 | 20.9466 | 2.4072 |  | 3.6114 | 50.4221 | 8.575 | 5.8801
| 25 | 16.8369 | 2.3868 |  | 4.4044 | 40.187 | 7.7875 | 5.1605
| 26 | 16.7533 | 2.1877 |  | 3.4245 | 36.651 | 8.575 | 4.2742
| 27 | 16.6139 | 2.3522 |  | 1.9803 | 39.0788 | 10.15 | 3.8501
| 28 | 16.7441 | 2.2975 |  | 1.8311 | 38.4695 | 10.15 | 3.7901
| 31 | 16.6975 | 2.1394 |  | 1.7572 | 35.7232 | 10.15 | 3.5195
| 31 | 16.6389 | 2.4142 |  | 1.9822 | 40.1704 | 10.15 | 3.9577
| AVG | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | 0 | 0 | 0
| MAX | 0 | 0 | 0 | 0 | 0 | 0 | 0
| MIN | 0 | 0 | 0 | 0 | 0 | 0 | 0